## Master (GD)
Internal | [9 empty] | A |  | B | C |  |  |  | D | E
Internal | [9 empty] | 28 | 136 | 28 | 6 | 5 | 136 | 136 | 39 | 106 | 14
Internal | [9 empty] | 101A | Inc in 111 | 104A | 105A (x) | 106A+B | 111A | 111B | Inc in 111 | Inc in 111 | HSE | Used to group |  |  |  | Template
Sorted No. | Init No. | Tag No. | S/N | GD TYPE | WINDOW | WP | UNIT | AREA | SUBSYSTEM | Instrument cable (101A) | Calibration (103A) | Junction box (104A) | Instrument tubing (105A) | Elec Panel (106A+B) | FG Device (111A) | FG Device (111B) | Cable Tray ladder (112A) | Stanchion | Scaffold | Common ITR | internal Grouping | Test Pack Numbering | Rev Test Pack Numbering | ITR Cat
1 | 1 | 65GA-106 | 3048820 | CH4 3W | 1_Before TA | 57 | 11 | 1A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | A1 | 57-11-TP620-I001-HES | WP57-11-TP620-I001-HES | ABDE
2 | 2 | 65GA-107 | 3046101 | CH4 3W | 1_Before TA | 57 | 11 | 1A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | A1 | 57-11-TP620-I001-HES | WP57-11-TP620-I001-HES | ABDE
3 | 4 | 65GA-110 | 3046098 | CH4 3W | 1_Before TA | 57 | 11 | 1A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | A1 | 57-11-TP620-I001-HES | WP57-11-TP620-I001-HES | ABDE
4 | 6 | 65GA-115 | 3050804 | CH4 3W | 1_Before TA | 57 | 11 | 1A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | A1 | 57-11-TP620-I001-HES | WP57-11-TP620-I001-HES | ABDE
5 | 3 | 65GA-108 | 3046099 | CH4 3W | 1_Before TA | 57 | 11 | 1A | 620 |  | Y |  |  |  | Y | Y | Y | Y |  | DE | A2 | 57-11-TP620-I002-HES | WP57-11-TP620-I002-HES | DE
6 | 10 | 65GA-121 | 3050767 | CH4 3W | 1_Before TA | 57 | 11 | 1A | 620 |  | Y |  |  |  | Y | Y | Y | Y |  | DE | A2 | 57-11-TP620-I002-HES | WP57-11-TP620-I002-HES | DE
7 | 5 | 65GA-111 | 3050785 | CH4 3W | 1_Before TA | 57 | 11 | 1A | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | A3 | 57-11-TP620-I003-HES | WP57-11-TP620-I003-HES | DE
8 | 7 | 65GA-116 | 3048810 | CH4 3W | 1_Before TA | 57 | 11 | 1A | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | A3 | 57-11-TP620-I003-HES | WP57-11-TP620-I003-HES | DE
9 | 8 | 65GA-119 | 3048828 | CH4 3W | 1_Before TA | 57 | 11 | 1A | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | A3 | 57-11-TP620-I003-HES | WP57-11-TP620-I003-HES | DE
10 | 9 | 65GA-120 | 3049423 | CH4 3W | 1_Before TA | 57 | 11 | 1A | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | A3 | 57-11-TP620-I003-HES | WP57-11-TP620-I003-HES | DE
11 | 66 | 65H2-120 | 3048032 | H2 3W | 1_Before TA | 57 | 11 | 1A | 620 |  | Y |  |  |  | Y | Y |  |  | Y |  | A4 | 57-11-TP620-I004-HES | WP57-11-TP620-I004-HES | DE
12 | 51 | 65GA-601 | AXGK2300184 | H2S 2W | 1_Before TA | 57 | 11 | 1A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | A5 | 57-11-TP620-I005-HES | WP57-11-TP620-I005-HES | DE
13 | 68 | 65H2S-101 | 3041318 | H2S 3W | 1_Before TA | 57 | 11 | 1A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | A6 | 57-11-TP620-I006-HES | WP57-11-TP620-I006-HES | ABDE
14 | 69 | 65H2S-102 | 3041383 | H2S 3W | 1_Before TA | 57 | 11 | 1A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | A6 | 57-11-TP620-I006-HES | WP57-11-TP620-I006-HES | ABDE
15 | 70 | 65H2S-103 | 3046075 | H2S 3W | 1_Before TA | 57 | 11 | 1A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | A6 | 57-11-TP620-I006-HES | WP57-11-TP620-I006-HES | ABDE
16 | 71 | 65H2S-104 | 3046084 | H2S 3W | 1_Before TA | 57 | 11 | 1A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | A6 | 57-11-TP620-I006-HES | WP57-11-TP620-I006-HES | ABDE
17 | 72 | 65H2S-107 | 3047355 | H2S 3W | 1_Before TA | 57 | 11 | 1A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | A6 | 57-11-TP620-I006-HES | WP57-11-TP620-I006-HES | ABDE
18 | 15 | 65GA-129 | 3048816 | CH4 3W | 1_Before TA | 57 | 12 | 1B | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | B1 | 57-12-TP620-I001-HES | WP57-12-TP620-I001-HES | DE
19 | 54 | 65H2-104 | 3048022 | H2 3W | 1_Before TA | 57 | 12 | 1B | 620 |  | Y |  |  |  | Y | Y |  |  | Y |  | B2 | 57-12-TP620-I002-HES | WP57-12-TP620-I002-HES | DE
20 | 60 | 65H2-112 | 3048033 | H2 3W | 1_Before TA | 57 | 12 | 1B | 620 |  | Y |  |  |  | Y | Y |  |  | Y |  | B2 | 57-12-TP620-I002-HES | WP57-12-TP620-I002-HES | DE
21 | 61 | 65H2-113 | 3048017 | H2 3W | 1_Before TA | 57 | 12 | 1B | 620 |  | Y |  |  |  | Y | Y |  |  | Y |  | B2 | 57-12-TP620-I002-HES | WP57-12-TP620-I002-HES | DE
22 | 62 | 65H2-114 | 3048030 | H2 3W | 1_Before TA | 57 | 12 | 1B | 620 |  | Y |  |  |  | Y | Y |  |  | Y |  | B2 | 57-12-TP620-I002-HES | WP57-12-TP620-I002-HES | DE
23 | 63 | 65H2-115 | 3048020 | H2 3W | 1_Before TA | 57 | 12 | 1B | 620 |  | Y |  |  |  | Y | Y |  |  | Y |  | B2 | 57-12-TP620-I002-HES | WP57-12-TP620-I002-HES | DE
24 | 52 | 65H2-101 | 3048028 | H2 3W | 1_Before TA | 57 | 12 | 1B | 620 |  | Y |  |  |  | Y | Y | Y | Y |  | DE | B3 | 57-12-TP620-I003-HES | WP57-12-TP620-I003-HES | DE
25 | 53 | 65H2-103 | 3048010 | H2 3W | 1_Before TA | 57 | 12 | 1B | 620 |  | Y |  |  |  | Y | Y | Y | Y |  | DE | B3 | 57-12-TP620-I003-HES | WP57-12-TP620-I003-HES | DE
26 | 75 | 65H2S-118 | 3047395 | H2S 3W | 1_Before TA | 57 | 12 | 1B | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | B4 | 57-12-TP620-I004-HES | WP57-12-TP620-I004-HES | ABDE
27 | 76 | 65H2S-119 | 3046078 | H2S 3W | 1_Before TA | 57 | 12 | 1B | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | B4 | 57-12-TP620-I004-HES | WP57-12-TP620-I004-HES | ABDE
28 | 77 | 65H2S-120 | 3046088 | H2S 3W | 1_Before TA | 57 | 12 | 1B | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | B4 | 57-12-TP620-I004-HES | WP57-12-TP620-I004-HES | ABDE
29 | 73 | 65H2S-111 | 3047309 | H2S 3W | 1_Before TA | 57 | 12 | 1B | 620 |  | Y |  |  |  | Y | Y | Y | Y |  | DE | B5 | 57-12-TP620-I005-HES | WP57-12-TP620-I005-HES | DE
30 | 74 | 65H2S-114 | 3046083 | H2S 3W | 1_Before TA | 57 | 12 | 1B | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | B6 | 57-12-TP620-I006-HES | WP57-12-TP620-I006-HES | DE
31 | 22 | 65GA-170 | 3050789 | CH4 3W | 1_Before TA | 57 | 13 | 1B | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | C1 | 57-13-TP620-I001-HES | WP57-13-TP620-I001-HES | DE
32 | 16 | 65GA-132 | 3048813 | CH4 3W | 1_Before TA | 57 | 13 | 1B | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | C2 | 57-13-TP620-I002-HES | WP57-13-TP620-I002-HES | ABDE
33 | 18 | 65GA-137 | 3048808 | CH4 3W | 1_Before TA | 57 | 13 | 1B | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | C2 | 57-13-TP620-I002-HES | WP57-13-TP620-I002-HES | ABDE
34 | 17 | 65GA-134 | 3046115 | CH4 3W | 1_Before TA | 57 | 13 | 1B | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | C3 | 57-13-TP620-I003-HES | WP57-13-TP620-I003-HES | DE
35 | 19 | 65GA-139 | 3048830 | CH4 3W | 1_Before TA | 57 | 13 | 1B | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | C3 | 57-13-TP620-I003-HES | WP57-13-TP620-I003-HES | DE
36 | 65 | 65H2-118 | 3048025 | H2 3W | 1_Before TA | 57 | 13 | 1B | 620 |  | Y |  |  |  | Y | Y |  |  | Y |  | C4 | 57-13-TP620-I004-HES | WP57-13-TP620-I004-HES | DE
37 | 55 | 65H2-106 | 3048024 | H2 3W | 1_Before TA | 57 | 13 | 1B | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | C5 | 57-13-TP620-I005-HES | WP57-13-TP620-I005-HES | ABDE
38 | 64 | 65H2-116 | 3048018 | H2 3W | 1_Before TA | 57 | 13 | 1B | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | C5 | 57-13-TP620-I005-HES | WP57-13-TP620-I005-HES | ABDE
39 | 56 | 65H2-107 | 3048053 | H2 3W | 1_Before TA | 57 | 13 | 1B | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | C6 | 57-13-TP620-I006-HES | WP57-13-TP620-I006-HES | DE
40 | 57 | 65H2-108 | 3048027 | H2 3W | 1_Before TA | 57 | 13 | 1B | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | C6 | 57-13-TP620-I006-HES | WP57-13-TP620-I006-HES | DE
41 | 58 | 65H2-109 | 3048006 | H2 3W | 1_Before TA | 57 | 13 | 1B | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | C6 | 57-13-TP620-I006-HES | WP57-13-TP620-I006-HES | DE
42 | 59 | 65H2-111 | 3048026 | H2 3W | 1_Before TA | 57 | 13 | 1B | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | C6 | 57-13-TP620-I006-HES | WP57-13-TP620-I006-HES | DE
43 | 11 | 65GA-125 | 3046113 | CH4 3W | 1_Before TA | 57 | 14 | 1A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | D | 57-14-TP620-I001-HES | WP57-14-TP620-I001-HES | ABDE
44 | 12 | 65GA-126 | 3048829 | CH4 3W | 1_Before TA | 57 | 14 | 1A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | D | 57-14-TP620-I001-HES | WP57-14-TP620-I001-HES | ABDE
45 | 13 | 65GA-127 | 3049419 | CH4 3W | 1_Before TA | 57 | 14 | 1A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | D | 57-14-TP620-I001-HES | WP57-14-TP620-I001-HES | ABDE
46 | 14 | 65GA-128 | 3049437 | CH4 3W | 1_Before TA | 57 | 14 | 1A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | D | 57-14-TP620-I001-HES | WP57-14-TP620-I001-HES | ABDE
47 | 78 | 65H2S-122 | 3047392 | H2S 3W | 1_Before TA | 57 | 15 | 1A | 620 |  | Y |  |  |  | Y | Y | Y | Y |  | DE | E | 57-15-TP620-I001-HES | WP57-15-TP620-I001-HES | DE
48 | 124 | 65XA-8154 | 3046116 | CH4 3W | 3_After TA | 57 | 18 | 6 | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | F1 | 57-18-TP620-I001-HES | WP57-18-TP620-I001-HES | DE
49 | 127 | 65XA-8157 | 3048812 | CH4 3W | 3_After TA | 57 | 18 | 6 | 620 |  | Y |  |  |  | Y | Y | Y | Y |  | DE | F2 | 57-18-TP620-I002-HES | WP57-18-TP620-I002-HES | DE
50 | 129 | 65XA-8160 | 3050783 | CH4 3W | 3_After TA | 57 | 18 | 6 | 620 |  | Y |  |  |  | Y | Y | Y | Y |  | DE | F2 | 57-18-TP620-I002-HES | WP57-18-TP620-I002-HES | DE
51 | 130 | 65XA-8162 | 3049417 | CH4 3W | 3_After TA | 57 | 18 | 6 | 620 |  | Y |  |  |  | Y | Y | Y | Y |  | DE | F2 | 57-18-TP620-I002-HES | WP57-18-TP620-I002-HES | DE
52 | 125 | 65XA-8155 | 3048009 | H2 3W | 3_After TA | 57 | 18 | 6 | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | F3 | 57-18-TP620-I003-HES | WP57-18-TP620-I003-HES | DE
53 | 128 | 65XA-8159 | 3047997 | H2 3W | 3_After TA | 57 | 18 | 6 | 620 |  | Y |  |  |  | Y | Y | Y | Y |  | DE | F4 | 57-18-TP620-I004-HES | WP57-18-TP620-I004-HES | DE
54 | 121 | 65XA-8151 | AXGK2300194 | H2S 2W | 3_After TA | 57 | 18 | 6 | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | F5 | 57-18-TP620-I005-HES | WP57-18-TP620-I005-HES | DE
55 | 126 | 65XA-8156 | AXGK2300190 | H2S 2W | 3_After TA | 57 | 18 | 6 | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | F5 | 57-18-TP620-I005-HES | WP57-18-TP620-I005-HES | DE
56 | 122 | 65XA-8152 | AXGK2300197 | H2S 2W | 3_After TA | 57 | 18 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | F6 | 57-18-TP620-I006-HES | WP57-18-TP620-I006-HES | DE
57 | 123 | 65XA-8153 | AXGK2300188 | H2S 2W | 3_After TA | 57 | 18 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | F6 | 57-18-TP620-I006-HES | WP57-18-TP620-I006-HES | DE
58 | 120 | 65XA-8144 | 3050764 | CH4 3W | 2_TA | 57 | 19 | 6 | 620 |  | Y |  | Y |  | Y | Y |  | Y | Y | CE | G1 | 57-19-TP620-I001-HES | WP57-19-TP620-I001-HES | DE
59 | 112 | 65XA-8136 | 3050787 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y | Y | Y |  | DE | G2 | 57-19-TP620-I002-HES | WP57-19-TP620-I002-HES | DE
60 | 113 | 65XA-8137 | 3046095 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y | Y | Y |  | DE | G2 | 57-19-TP620-I002-HES | WP57-19-TP620-I002-HES | DE
61 | 94 | 65XA-8115 | 3049440 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G3 | 57-19-TP620-I003-HES | WP57-19-TP620-I003-HES | DE
62 | 95 | 65XA-8116 | 3049426 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G3 | 57-19-TP620-I003-HES | WP57-19-TP620-I003-HES | DE
63 | 96 | 65XA-8120 | 3046110 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G3 | 57-19-TP620-I003-HES | WP57-19-TP620-I003-HES | DE
64 | 97 | 65XA-8121 | 3046111 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G3 | 57-19-TP620-I003-HES | WP57-19-TP620-I003-HES | DE
65 | 98 | 65XA-8122 | 3050776 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G4 | 57-19-TP620-I004-HES | WP57-19-TP620-I004-HES | DE
66 | 99 | 65XA-8123 | 3046109 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G4 | 57-19-TP620-I004-HES | WP57-19-TP620-I004-HES | DE
67 | 100 | 65XA-8124 | 3046100 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G4 | 57-19-TP620-I004-HES | WP57-19-TP620-I004-HES | DE
68 | 101 | 65XA-8125 | 3046123 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G4 | 57-19-TP620-I004-HES | WP57-19-TP620-I004-HES | DE
69 | 102 | 65XA-8126 | 3046087 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G5 | 57-19-TP620-I005-HES | WP57-19-TP620-I005-HES | DE
70 | 103 | 65XA-8127 | 3048807 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G5 | 57-19-TP620-I005-HES | WP57-19-TP620-I005-HES | DE
71 | 104 | 65XA-8128 | 3046114 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G5 | 57-19-TP620-I005-HES | WP57-19-TP620-I005-HES | DE
72 | 105 | 65XA-8129 | 3049413 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G5 | 57-19-TP620-I005-HES | WP57-19-TP620-I005-HES | DE
73 | 106 | 65XA-8130 | 3033005 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G6 | 57-19-TP620-I006-HES | WP57-19-TP620-I006-HES | DE
74 | 107 | 65XA-8131 | 3050769 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G6 | 57-19-TP620-I006-HES | WP57-19-TP620-I006-HES | DE
75 | 108 | 65XA-8132 | 3046103 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G6 | 57-19-TP620-I006-HES | WP57-19-TP620-I006-HES | DE
76 | 109 | 65XA-8133 | 3046105 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G6 | 57-19-TP620-I006-HES | WP57-19-TP620-I006-HES | DE
77 | 110 | 65XA-8134 | 3048806 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G7 | 57-19-TP620-I007-HES | WP57-19-TP620-I007-HES | DE
78 | 111 | 65XA-8135 | 3048817 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G7 | 57-19-TP620-I007-HES | WP57-19-TP620-I007-HES | DE
79 | 114 | 65XA-8138 | 3048811 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G7 | 57-19-TP620-I007-HES | WP57-19-TP620-I007-HES | DE
80 | 118 | 65XA-8142 | 3045776 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G7 | 57-19-TP620-I007-HES | WP57-19-TP620-I007-HES | DE
81 | 119 | 65XA-8143 | 3048822 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G7 | 57-19-TP620-I007-HES | WP57-19-TP620-I007-HES | DE
82 | 92 | 65XA-8113 | 3048029 | H2 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G8 | 57-19-TP620-I008-HES | WP57-19-TP620-I008-HES | DE
83 | 93 | 65XA-8114 | 3048052 | H2 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G8 | 57-19-TP620-I008-HES | WP57-19-TP620-I008-HES | DE
84 | 84 | 65XA-8101 | AXGK2300196 | H2S 2W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G9 | 57-19-TP620-I009-HES | WP57-19-TP620-I009-HES | DE
85 | 85 | 65XA-8102 | AXGK2300186 | H2S 2W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G9 | 57-19-TP620-I009-HES | WP57-19-TP620-I009-HES | DE
86 | 86 | 65XA-8103 | AXGK2300187 | H2S 2W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G9 | 57-19-TP620-I009-HES | WP57-19-TP620-I009-HES | DE
87 | 87 | 65XA-8104 | AXGK2300189 | H2S 2W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G9 | 57-19-TP620-I009-HES | WP57-19-TP620-I009-HES | DE
88 | 88 | 65XA-8105 | AXGK2300192 | H2S 2W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G10 | 57-19-TP620-I010-HES | WP57-19-TP620-I010-HES | DE
89 | 89 | 65XA-8106 | AXGK2300193 | H2S 2W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G10 | 57-19-TP620-I010-HES | WP57-19-TP620-I010-HES | DE
90 | 115 | 65XA-8139 | AXGK2300195 | H2S 2W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G10 | 57-19-TP620-I010-HES | WP57-19-TP620-I010-HES | DE
91 | 116 | 65XA-8140 | AXGK2300185 | H2S 2W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G10 | 57-19-TP620-I010-HES | WP57-19-TP620-I010-HES | DE
92 | 117 | 65XA-8141 | AXGK2300191 | H2S 2W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G10 | 57-19-TP620-I010-HES | WP57-19-TP620-I010-HES | DE
93 | 90 | 65XA-8111 | 3047363 | H2S 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G11 | 57-19-TP620-I011-HES | WP57-19-TP620-I011-HES | DE
94 | 91 | 65XA-8112 | 3047367 | H2S 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G11 | 57-19-TP620-I011-HES | WP57-19-TP620-I011-HES | DE
95 | 67 | 65H2-121 | 3048021 | H2 3W | 1_Before TA | 57 | 51 | 5A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y | Y | ABDE | H | 57-51-TP620-I001-HES | WP57-51-TP620-I001-HES | ABDE
96 | 80 | 65H2S-129 | 3047358 | H2S 3W | 1_Before TA | 57 | 64 | 5A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | I1 | 57-64-TP620-I001-HES | WP57-64-TP620-I001-HES | ABDE
97 | 79 | 65H2S-128 | 3046091 | H2S 3W | 1_Before TA | 57 | 64 | 5A | 620 |  | Y |  |  |  | Y | Y | Y | Y |  | DE | I2 | 57-64-TP620-I002-HES | WP57-64-TP620-I002-HES | DE
98 | 23 | 65GA-201 | 3048819 | CH4 3W | 1_Before TA | 57 | 66 | 4A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | J1 | 57-66-TP620-I001-HES | WP57-66-TP620-I001-HES | ABDE
99 | 49 | 65GA-270 | 3049432 | CH4 3W | 1_Before TA | 57 | 66 | 4A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | J1 | 57-66-TP620-I001-HES | WP57-66-TP620-I001-HES | ABDE
100 | 50 | 65GA-274 | 3050790 | CH4 3W | 1_Before TA | 57 | 66 | 4A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | J1 | 57-66-TP620-I001-HES | WP57-66-TP620-I001-HES | ABDE
101 | 25 | 65GA-206 | 3048804 | CH4 3W | 1_Before TA | 57 | 71 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | K1 | 57-71-TP620-I001-HES | WP57-71-TP620-I001-HES | DE
102 | 44 | 65GA-245 | 3046097 | CH4 3W | 1_Before TA | 57 | 71 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | K1 | 57-71-TP620-I001-HES | WP57-71-TP620-I001-HES | DE
103 | 45 | 65GA-246 | 3049934 | CH4 3W | 1_Before TA | 57 | 71 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | K1 | 57-71-TP620-I001-HES | WP57-71-TP620-I001-HES | DE
104 | 46 | 65GA-249 | 3046120 | CH4 3W | 1_Before TA | 57 | 71 | 4A | 620 | Y | Y | Y |  |  | Y | Y |  | Y |  | ABE | K2 | 57-71-TP620-I002-HES | WP57-71-TP620-I002-HES | ABDE
105 | 24 | 65GA-205 | 3050796 | CH4 3W | 1_Before TA | 57 | 71 | 4A | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | K3 | 57-71-TP620-I003-HES | WP57-71-TP620-I003-HES | DE
106 | 26 | 65GA-207 | 3048814 | CH4 3W | 1_Before TA | 57 | 71 | 4A | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | K3 | 57-71-TP620-I003-HES | WP57-71-TP620-I003-HES | DE
107 | 33 | 65GA-225 | 3046117 | CH4 3W | 1_Before TA | 57 | 73 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | L1 | 57-73-TP620-I001-HES | WP57-73-TP620-I001-HES | DE
108 | 36 | 65GA-229 | 3048827 | CH4 3W | 1_Before TA | 57 | 73 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | L1 | 57-73-TP620-I001-HES | WP57-73-TP620-I001-HES | DE
109 | 37 | 65GA-230 | 3048832 | CH4 3W | 1_Before TA | 57 | 73 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | L1 | 57-73-TP620-I001-HES | WP57-73-TP620-I001-HES | DE
110 | 38 | 65GA-231 | 3050792 | CH4 3W | 1_Before TA | 57 | 73 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | L1 | 57-73-TP620-I001-HES | WP57-73-TP620-I001-HES | DE
111 | 39 | 65GA-232 | 3050774 | CH4 3W | 1_Before TA | 57 | 73 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | L2 | 57-73-TP620-I002-HES | WP57-73-TP620-I002-HES | DE
112 | 40 | 65GA-233 | 3049435 | CH4 3W | 1_Before TA | 57 | 73 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | L2 | 57-73-TP620-I002-HES | WP57-73-TP620-I002-HES | DE
113 | 41 | 65GA-234 | 3049428 | CH4 3W | 1_Before TA | 57 | 73 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | L2 | 57-73-TP620-I002-HES | WP57-73-TP620-I002-HES | DE
114 | 42 | 65GA-236 | 3049427 | CH4 3W | 1_Before TA | 57 | 73 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | L2 | 57-73-TP620-I002-HES | WP57-73-TP620-I002-HES | DE
115 | 34 | 65GA-226 | 3046118 | CH4 3W | 1_Before TA | 57 | 73 | 4A | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | L3 | 57-73-TP620-I003-HES | WP57-73-TP620-I003-HES | DE
116 | 27 | 65GA-215 | 3050762 | CH4 3W | 1_Before TA | 57 | 75 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | M1 | 57-75-TP620-I001-HES | WP57-75-TP620-I001-HES | DE
117 | 28 | 65GA-216 | 3046077 | CH4 3W | 1_Before TA | 57 | 75 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | M1 | 57-75-TP620-I001-HES | WP57-75-TP620-I001-HES | DE
118 | 30 | 65GA-220 | 3049439 | CH4 3W | 1_Before TA | 57 | 75 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | M1 | 57-75-TP620-I001-HES | WP57-75-TP620-I001-HES | DE
119 | 31 | 65GA-221 | 3050809 | CH4 3W | 1_Before TA | 57 | 75 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | M1 | 57-75-TP620-I001-HES | WP57-75-TP620-I001-HES | DE
120 | 32 | 65GA-223 | 3046104 | CH4 3W | 1_Before TA | 57 | 75 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | M1 | 57-75-TP620-I001-HES | WP57-75-TP620-I001-HES | DE
121 | 29 | 65GA-218 | 3046094 | CH4 3W | 1_Before TA | 57 | 75 | 4A | 620 | Y | Y | Y |  |  | Y | Y |  | Y |  | ABE | M2 | 57-75-TP620-I002-HES | WP57-75-TP620-I002-HES | ABDE
122 | 47 | 65GA-250 | 3049416 | CH4 3W | 1_Before TA | 57 | 75 | 4A | 620 |  | Y |  |  |  | Y | Y | Y | Y |  | DE | M3 | 57-75-TP620-I003-HES | WP57-75-TP620-I003-HES | DE
123 | 35 | 65GA-228 | 3049412 | CH4 3W | 1_Before TA | 57 | 75 | 4A | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | M4 | 57-75-TP620-I004-HES | WP57-75-TP620-I004-HES | DE
124 | 43 | 65GA-240 | 3048826 | CH4 3W | 1_Before TA | 57 | 77 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | N1 | 57-77-TP620-I001-HES | WP57-77-TP620-I001-HES | DE
125 | 48 | 65GA-267 | 3048803 | CH4 3W | 1_Before TA | 57 | 77 | 4A | 620 | Y | Y | Y |  |  | Y | Y |  | Y |  | ABE | N2 | 57-77-TP620-I002-HES | WP57-77-TP620-I002-HES | ABDE
126 | 20 | 65GA-151B | 3050781 | CH4 3W | 2_TA | 57 | MCB | MCB | 620 |  | Y |  | Y |  | Y | Y |  | Y | Y | CE | O1 | 57-MCB-TP620-I001-HES | WP57-MCB-TP620-I001-HES | DE
127 | 21 | 65GA-151C | 3050768 | CH4 3W | 2_TA | 57 | MCB | MCB | 620 |  | Y |  | Y |  | Y | Y |  | Y | Y | CE | O1 | 57-MCB-TP620-I001-HES | WP57-MCB-TP620-I001-HES | DE
128 | 81 | 65XA-2631 | AXGK2300210 | H2S 2W | 2_TA | 57 | MCB | MCB | 620 |  | Y |  | Y |  | Y | Y |  | Y | Y | CE | O2 | 57-MCB-TP620-I002-HES | WP57-MCB-TP620-I002-HES | DE
129 | 82 | 65XA-2632 | AXGK2300211 | H2S 2W | 2_TA | 57 | MCB | MCB | 620 |  | Y |  | Y |  | Y | Y |  | Y | Y | CE | O2 | 57-MCB-TP620-I002-HES | WP57-MCB-TP620-I002-HES | DE
130 | 83 | 65XA-2633 | AXGK2300212 | H2S 2W | 2_TA | 57 | MCB | MCB | 620 |  | Y |  | Y |  | Y | Y |  | Y | Y | CE | O2 | 57-MCB-TP620-I002-HES | WP57-MCB-TP620-I002-HES | DE
131 | 134 | 65XA-8193A | 3049441 | CH4 3W | 2_TA | 57 | SCR8 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | P2 | 57-SCR8-TP620-I002-HES | WP57-SCR8-TP620-I002-HES | DE
132 | 135 | 65XA-8193B | 3049420 | CH4 3W | 2_TA | 57 | SCR8 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | P2 | 57-SCR8-TP620-I002-HES | WP57-SCR8-TP620-I002-HES | DE
133 | 136 | 65XA-8193C | 3048818 | CH4 3W | 2_TA | 57 | SCR8 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | P2 | 57-SCR8-TP620-I002-HES | WP57-SCR8-TP620-I002-HES | DE
134 | 131 | 65XA-8190A | AXGK2300203 | H2S 2W | 2_TA | 57 | SCR8 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | P1 | 57-SCR8-TP620-I001-HES | WP57-SCR8-TP620-I001-HES | DE
135 | 132 | 65XA-8190B | AXGK2300204 | H2S 2W | 2_TA | 57 | SCR8 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | P1 | 57-SCR8-TP620-I001-HES | WP57-SCR8-TP620-I001-HES | DE
136 | 133 | 65XA-8190C | AXGK2300205 | H2S 2W | 2_TA | 57 | SCR8 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | P1 | 57-SCR8-TP620-I001-HES | WP57-SCR8-TP620-I001-HES | DE
137 | 137 | MCB-FGS-001 SYSTEM, MCB-FGS-001 MDF |  | Cab | 2_TA | 57 | MCB | MCB | 620 |  |  |  |  | Y | [7 empty] | 57-MCB-TP620-I003-HES | WP57-MCB-TP620-I003-HES | C
138 | 138 | OMS-FGS-001 SYSTEM, OMS-FGS-001 MDF |  | Cab | 2_TA | 57 | OMS | 4A | 620 |  |  |  |  | Y | [7 empty] | 57-OMS-TP620-I001-HES | WP57-OMS-TP620-I001-HES | C
139 | 139 | SS1-FGS-001 SYSTEM, SS1-FGS-001 MDF |  | Cab | 2_TA | 57 | SS01 | 4A | 620 |  |  |  |  | Y | [7 empty] | 57-SS1-TP620-I001-HES | WP57-SS1-TP620-I001-HES | C
140 | 140 | SS7-FGS-001 SYSTEM, SS7-FGS-001 MDF |  | Cab | 2_TA | 57 | SS07 | 4A | 620 |  |  |  |  | Y | [7 empty] | 57-SS7-TP620-I001-HES | WP57-SS7-TP620-I001-HES | C
141 | 141 | 8-FGS-001 SYSTEM, 8-FGS-002 SYSTEM, 8-MDF-001, 8-MDF-002, 8-MDF-003 |  | Cab | 2_TA | 57 | SCR8 | 6 | 620 |  |  |  |  | Y | [7 empty] | 57-SCR8-TP620-I003-HES | WP57-SCR8-TP620-I003-HES | C

## Master (GD)_Detailed ITR
Internal
[16 empty] | 111A |  |  |  |  | 101A |  |  |  | 104A | [6 empty] | 111B
Sorted No. | Tag No. | S/N | GD TYPE | WINDOW | UNIT | AREA | AREA/UNIT | SUBSYSTEM | SUB-SUBSYSTEM | CATEGORY | Number of tags | Template | TEST PACK NO | REV TEST PACK NO | File Name | MANUFACTURER | SIZE (KG) | MODEL NO | Set point pressure | Datasheet | Cable Size | Voltage | Cable from (Int JB) | Cable To (GD) | IP Rating (JB) | Manufacturer | DWG no. | EX Class | Location | Serial No. | Type | Mode of Detection | EX Protection | Model No | Serial No. | Signal Range (mA, EU) | IP Rating | Manufacturer | DWG No.
1 | 65GA-106, 65GA-107, 65GA-110, 65GA-115 | 3048820 (106), 3046101 (107), 3046098 (110), 3050804 (115) | CH4 3W | OSTA 23 | 11 | 1A | AREA 1A / UNIT 11 | 620 | 622 | 4 | 4 | 4_4 | 57-11-TP620-I001-HES | WP57-11-TP620-I001-HES | 1_WP57-11-TP620-I001-HES (65GA-106, 65GA-107, 65GA-110, 65GA-115) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | 1Tr x 1.5mm2, 3 Cores | 500V | 11-JB-GA106, 11-JB-GA107, 11-JB-GA110, 11-JB-GA115 | 65GA-106, 65GA-107, 65GA-110, 65GA-115 | IP66 | PHOENIX CONTACT | RESET-EXE-HES-00-MCI-MAF-4003 | Ex II 2G Ex e II T6/T5 | Area 1A / Unit 11 |  | Wall mount | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3048820 (106), 3046101 (107), 3046098 (110), 3050804 (115) | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-1A-INC-LST-4001
2 | 65GA-108, 65GA-121 | 3046099 (108), 3050767 (121) | CH4 3W | OSTA 23 | 11 | 1A | AREA 1A / UNIT 11 | 620 | 622 | 2 | 2 | 2_2 | 57-11-TP620-I002-HES | WP57-11-TP620-I002-HES | 2_WP57-11-TP620-I002-HES (65GA-108, 65GA-121) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3046099 (108), 3050767 (121) | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-1A-INC-LST-4001
3 | 65GA-111, 65GA-116, 65GA-119, 65GA-120 | 3050785 (111), 3048810 (116), 3048828 (119), 3049423 (120) | CH4 3W | OSTA 23 | 11 | 1A | AREA 1A / UNIT 11 | 620 | 622 | 2 | 4 | 2_4 | 57-11-TP620-I003-HES | WP57-11-TP620-I003-HES | 3_WP57-11-TP620-I003-HES (65GA-111, 65GA-116, 65GA-119, 65GA-120) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3050785 (111), 3048810 (116), 3048828 (119), 3049423 (120) | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-1A-INC-LST-4001
4 | 65H2-120 | 3048032 | H2 3W | OSTA 23 | 11 | 1A | AREA 1A / UNIT 11 | 620 | 622 | 2 | 1 | 2_1 | 57-11-TP620-I004-HES | WP57-11-TP620-I004-HES | 4_WP57-11-TP620-I004-HES (65H2-120) | GASENSOR | 4.8KG | HE-CT8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, low temperature catalytic bead | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CT8900 | 3048032 | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-1A-INC-LST-4001
5 | 65GA-601 | AXGK2300184 | H2S 2W | OSTA 23 | 11 | 1A | AREA 1A / UNIT 11 | 620 | 622 | 2 | 1 | 2_1 | 57-11-TP620-I005-HES | WP57-11-TP620-I005-HES | 5_WP57-11-TP620-I005-HES (65GA-601) | GASTRON | 2KG | GTD-2000TX | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | GTD-2000TX | AXGK2300184 | 0-20mA, -12.5-50 PPM | IP66 | GASTRON | RESET-EXE-HES-1A-INC-LST-4001
6 | 65H2S-101, 65H2S-102, 65H2S-103, 65H2S-104, 65H2S-107 | 3041318 (101), 3041383 (102), 3046075 (103), 3046084 (104), 3047355 (107) | H2S 3W | OSTA 23 | 11 | 1A | AREA 1A / UNIT 11 | 620 | 622 | 4 | 5 | 4_5 | 57-11-TP620-I006-HES | WP57-11-TP620-I006-HES | 6_WP57-11-TP620-I006-HES (65H2S-101, 65H2S-102, 65H2S-103, 65H2S-104, 65H2S-107) | GASENSOR | 4.8KG | HE-CE8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | 1Tr x 1.5mm2, 3 Cores | 500V | 11-JB-H2S101, 11-JB-H2S102, 11-JB-H2S103, 11-JB-H2S104, 11-JB-H2S107 | 65H2S-101, 65H2S-102, 65H2S-103, 65H2S-104, 65H2S-107 | IP66 | PHOENIX CONTACT | RESET-EXE-HES-00-MCI-MAF-4003 | Ex II 2G Ex e II T6/T5 | Area 1A / Unit 11 |  | Wall mount | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CE8900 | 3041318 (101), 3041383 (102), 3046075 (103), 3046084 (104), 3047355 (107) | 0-20mA, -12.5-50 PPM | IP66 | GASENSOR | RESET-EXE-HES-1A-INC-LST-4001
7 | 65GA-129 | 3048816 | CH4 3W | OSTA 23 | 12 | 1B | AREA 1B / UNIT 12 | 620 | 622 | 2 | 1 | 2_1 | 57-12-TP620-I001-HES | WP57-12-TP620-I001-HES | 7_WP57-12-TP620-I001-HES (65GA-129) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3048816 | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-1B-INC-LST-4001
8 | 65H2-104, 65H2-112, 65H2-113, 65H2-114, 65H2-115 | 3048022 (104), 3048033 (112), 3048017 (113), 3048030 (114), 3048020 (115) | H2 3W | OSTA 23 | 12 | 1B | AREA 1B / UNIT 12 | 620 | 622 | 2 | 5 | 2_5 | 57-12-TP620-I002-HES | WP57-12-TP620-I002-HES | 8_WP57-12-TP620-I002-HES (65H2-104, 65H2-112, 65H2-113, 65H2-114, 65H2-115) | GASENSOR | 4.8KG | HE-CT8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, low temperature catalytic bead | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CT8900 | 3048022 (104), 3048033 (112), 3048017 (113), 3048030 (114), 3048020 (115) | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-1B-INC-LST-4001
9 | 65H2-101, 65H2-103 | 3048028 (101), 3048010 (103) | H2 3W | OSTA 23 | 12 | 1B | AREA 1B / UNIT 12 | 620 | 622 | 2 | 2 | 2_2 | 57-12-TP620-I003-HES | WP57-12-TP620-I003-HES | 9_WP57-12-TP620-I003-HES (65H2-101, 65H2-103) | GASENSOR | 4.8KG | HE-CT8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, low temperature catalytic bead | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CT8900 | 3048028 (101), 3048010 (103) | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-1B-INC-LST-4001
10 | 65H2S-118, 65H2S-119, 65H2S-120 | 3047395 (118), 3046078 (119), 3046088 (120) | H2S 3W | OSTA 23 | 12 | 1B | AREA 1B / UNIT 12 | 620 | 622 | 4 | 3 | 4_3 | 57-12-TP620-I004-HES | WP57-12-TP620-I004-HES | 10_WP57-12-TP620-I004-HES (65H2S-118, 65H2S-119, 65H2S-120) | GASENSOR | 4.8KG | HE-CE8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | 1Tr x 1.5mm2, 3 Cores | 500V | 12-JB-H2S118, 12-JB-H2S119, 12-JB-H2S120 | 65H2S-118, 65H2S-119, 65H2S-120 | IP66 | PHOENIX CONTACT | RESET-EXE-HES-00-MCI-MAF-4003 | Ex II 2G Ex e II T6/T5 | Area 1B / Unit 12 |  | Wall mount | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CE8900 | 3047395 (118), 3046078 (119), 3046088 (120) | 0-20mA, -12.5-50 PPM | IP66 | GASENSOR | RESET-EXE-HES-1B-INC-LST-4001
11 | 65H2S-111 | 3047309 | H2S 3W | OSTA 23 | 12 | 1B | AREA 1B / UNIT 12 | 620 | 622 | 2 | 1 | 2_1 | 57-12-TP620-I005-HES | WP57-12-TP620-I005-HES | 11_WP57-12-TP620-I005-HES (65H2S-111) | GASENSOR | 4.8KG | HE-CE8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CE8900 | 3047309 | 0-20mA, -12.5-50 PPM | IP66 | GASENSOR | RESET-EXE-HES-1B-INC-LST-4001
12 | 65H2S-114 | 3046083 | H2S 3W | OSTA 23 | 12 | 1B | AREA 1B / UNIT 12 | 620 | 622 | 2 | 1 | 2_1 | 57-12-TP620-I006-HES | WP57-12-TP620-I006-HES | 12_WP57-12-TP620-I006-HES (65H2S-114) | GASENSOR | 4.8KG | HE-CE8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CE8900 | 3046083 | 0-20mA, -12.5-50 PPM | IP66 | GASENSOR | RESET-EXE-HES-1B-INC-LST-4001
13 | 65GA-170 | 3050789 | CH4 3W | OSTA 23 | 13 | 1B | AREA 1B / UNIT 13 | 620 | 622 | 2 | 1 | 2_1 | 57-13-TP620-I001-HES | WP57-13-TP620-I001-HES | 13_WP57-13-TP620-I001-HES (65GA-170) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3050789 | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-1B-INC-LST-4001
14 | 65GA-132, 65GA-137 | 3048813 (132), 3048808 (137) | CH4 3W | OSTA 23 | 13 | 1B | AREA 1B / UNIT 13 | 620 | 622 | 4 | 2 | 4_2 | 57-13-TP620-I002-HES | WP57-13-TP620-I002-HES | 14_WP57-13-TP620-I002-HES (65GA-132, 65GA-137) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | 1Tr x 1.5mm2, 3 Cores | 500V | 13-JB-GA132, 13-JB-GA137 | 65GA-132, 65GA-137 | IP66 | PHOENIX CONTACT | RESET-EXE-HES-00-MCI-MAF-4003 | Ex II 2G Ex e II T6/T5 | Area 1B / Unit 13 |  | Wall mount | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3048813 (132), 3048808 (137) | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-1B-INC-LST-4001
15 | 65GA-134, 65GA-139 | 3046115 (134), 3048830 (139) | CH4 3W | OSTA 23 | 13 | 1B | AREA 1B / UNIT 13 | 620 | 622 | 2 | 2 | 2_2 | 57-13-TP620-I003-HES | WP57-13-TP620-I003-HES | 15_WP57-13-TP620-I003-HES (65GA-134, 65GA-139) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3046115 (134), 3048830 (139) | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-1B-INC-LST-4001
16 | 65H2-118 | 3048025 | H2 3W | OSTA 23 | 13 | 1B | AREA 1B / UNIT 13 | 620 | 622 | 2 | 1 | 2_1 | 57-13-TP620-I004-HES | WP57-13-TP620-I004-HES | 16_WP57-13-TP620-I004-HES (65H2-118) | GASENSOR | 4.8KG | HE-CT8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, low temperature catalytic bead | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CT8900 | 3048025 | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-1B-INC-LST-4001
17 | 65H2-106, 65H2-116 | 3048024 (106), 3048018 (116) | H2 3W | OSTA 23 | 13 | 1B | AREA 1B / UNIT 13 | 620 | 622 | 4 | 2 | 4_2 | 57-13-TP620-I005-HES | WP57-13-TP620-I005-HES | 17_WP57-13-TP620-I005-HES (65H2-106, 65H2-116) | GASENSOR | 4.8KG | HE-CT8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | 1Tr x 1.5mm2, 3 Cores | 500V | 13-JB-H2106, 13-JB-H2116 | 65H2-106, 65H2-116 | IP66 | PHOENIX CONTACT | RESET-EXE-HES-00-MCI-MAF-4003 | Ex II 2G Ex e II T6/T5 | Area 1B / Unit 13 |  | Wall mount | Continuous diffusion, low temperature catalytic bead | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CT8900 | 3048024 (106), 3048018 (116) | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-1B-INC-LST-4001
18 | 65H2-107, 65H2-108, 65H2-109, 65H2-111 | 3048053 (107), 3048027 (108), 3048006 (109), 3048026 (111) | H2 3W | OSTA 23 | 13 | 1B | AREA 1B / UNIT 13 | 620 | 622 | 2 | 4 | 2_4 | 57-13-TP620-I006-HES | WP57-13-TP620-I006-HES | 18_WP57-13-TP620-I006-HES (65H2-107, 65H2-108, 65H2-109, 65H2-111) | GASENSOR | 4.8KG | HE-CT8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, low temperature catalytic bead | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CT8900 | 3048053 (107), 3048027 (108), 3048006 (109), 3048026 (111) | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-1B-INC-LST-4001
19 | 65GA-125, 65GA-126, 65GA-127, 65GA-128 | 3046113 (125), 3048829 (126), 3049419 (127), 3049437 (128) | CH4 3W | OSTA 23 | 14 | 1A | AREA 1A / UNIT 14 | 620 | 622 | 4 | 4 | 4_4 | 57-14-TP620-I001-HES | WP57-14-TP620-I001-HES | 19_WP57-14-TP620-I001-HES (65GA-125, 65GA-126, 65GA-127, 65GA-128) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | 1Tr x 1.5mm2, 3 Cores | 500V | 14-JB-GA125, 14-JB-GA126, 14-JB-GA127, 14-JB-GA128 | 65GA-125, 65GA-126, 65GA-127, 65GA-128 | IP66 | PHOENIX CONTACT | RESET-EXE-HES-00-MCI-MAF-4003 | Ex II 2G Ex e II T6/T5 | Area 1A / Unit 14 |  | Wall mount | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3046113 (125), 3048829 (126), 3049419 (127), 3049437 (128) | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-1A-INC-LST-4001
20 | 65H2S-122 | 3047392 | H2S 3W | OSTA 23 | 15 | 1A | AREA 1A / UNIT 15 | 620 | 622 | 2 | 1 | 2_1 | 57-15-TP620-I001-HES | WP57-15-TP620-I001-HES | 20_WP57-15-TP620-I001-HES (65H2S-122) | GASENSOR | 4.8KG | HE-CE8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CE8900 | 3047392 | 0-20mA, -12.5-50 PPM | IP66 | GASENSOR | RESET-EXE-HES-1A-INC-LST-4001
21 | 65XA-8154 | 3046116 | CH4 3W | OSTA 24 | 18 | 6 | AREA 6 / UNIT 18 | 620 | 622 | 2 | 1 | 2_1 | 57-18-TP620-I001-HES | WP57-18-TP620-I001-HES | 21_WP57-18-TP620-I001-HES (65XA-8154) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3046116 | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-06-INC-LST-4003
22 | 65XA-8157, 65XA-8160, 65XA-8162 | 3048812 (8157), 3050783 (8160), 3049417 (8162) | CH4 3W | OSTA 24 | 18 | 6 | AREA 6 / UNIT 18 | 620 | 622 | 2 | 3 | 2_3 | 57-18-TP620-I002-HES | WP57-18-TP620-I002-HES | 22_WP57-18-TP620-I002-HES (65XA-8157, 65XA-8160, 65XA-8162) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3048812 (8157), 3050783 (8160), 3049417 (8162) | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-06-INC-LST-4003
23 | 65XA-8155 | 3048009 | H2 3W | OSTA 24 | 18 | 6 | AREA 6 / UNIT 18 | 620 | 622 | 2 | 1 | 2_1 | 57-18-TP620-I003-HES | WP57-18-TP620-I003-HES | 23_WP57-18-TP620-I003-HES (65XA-8155) | GASENSOR | 4.8KG | HE-CT8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, low temperature catalytic bead | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CT8900 | 3048009 | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-06-INC-LST-4003
24 | 65XA-8159 | 3047997 | H2 3W | OSTA 24 | 18 | 6 | AREA 6 / UNIT 18 | 620 | 622 | 2 | 1 | 2_1 | 57-18-TP620-I004-HES | WP57-18-TP620-I004-HES | 24_WP57-18-TP620-I004-HES (65XA-8159) | GASENSOR | 4.8KG | HE-CT8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, low temperature catalytic bead | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CT8900 | 3047997 | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-06-INC-LST-4003
25 | 65XA-8151, 65XA-8156 | AXGK2300194 (8151), AXGK2300190 (8156) | H2S 2W | OSTA 24 | 18 | 6 | AREA 6 / UNIT 18 | 620 | 622 | 2 | 2 | 2_2 | 57-18-TP620-I005-HES | WP57-18-TP620-I005-HES | 25_WP57-18-TP620-I005-HES (65XA-8151, 65XA-8156) | GASTRON | 2KG | GTD-2000TX | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | GTD-2000TX | AXGK2300194 (8151), AXGK2300190 (8156) | 0-20mA, -12.5-50 PPM | IP66 | GASTRON | RESET-EXE-HES-06-INC-LST-4003
26 | 65XA-8152, 65XA-8153 | AXGK2300197 (8152), AXGK2300188 (8153) | H2S 2W | OSTA 24 | 18 | 6 | AREA 6 / UNIT 18 | 620 | 622 | 2 | 2 | 2_2 | 57-18-TP620-I006-HES | WP57-18-TP620-I006-HES | 26_WP57-18-TP620-I006-HES (65XA-8152, 65XA-8153) | GASTRON | 2KG | GTD-2000TX | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | GTD-2000TX | AXGK2300197 (8152), AXGK2300188 (8153) | 0-20mA, -12.5-50 PPM | IP66 | GASTRON | RESET-EXE-HES-06-INC-LST-4003
27 | 65XA-8144 | 3050764 | CH4 3W | TA 2024 | 19 | 6 | AREA 6 / UNIT 19 | 620 | 622 | 2 | 1 | 2_1 | 57-19-TP620-I001-HES | WP57-19-TP620-I001-HES | 27_WP57-19-TP620-I001-HES (65XA-8144) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3050764 | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-06-INC-LST-4003
28 | 65XA-8136, 65XA-8137 | 3050787 (8136), 3046095 (8137) | CH4 3W | OSTA 24 | 19 | 6 | AREA 6 / UNIT 19 | 620 | 622 | 2 | 2 | 2_2 | 57-19-TP620-I002-HES | WP57-19-TP620-I002-HES | 28_WP57-19-TP620-I002-HES (65XA-8136, 65XA-8137) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3050787 (8136), 3046095 (8137) | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-06-INC-LST-4003
29 | 65XA-8115, 65XA-8116, 65XA-8120, 65XA-8121 | 3049440 (8115), 3049426 (8116), 3046110 (8120), 3046111 (8121) | CH4 3W | OSTA 24 | 19 | 6 | AREA 6 / UNIT 19 | 620 | 622 | 2 | 4 | 2_4 | 57-19-TP620-I003-HES | WP57-19-TP620-I003-HES | 29_WP57-19-TP620-I003-HES (65XA-8115, 65XA-8116, 65XA-8120, 65XA-8121) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3049440 (8115), 3049426 (8116), 3046110 (8120), 3046111 (8121) | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-06-INC-LST-4003
30 | 65XA-8122, 65XA-8123, 65XA-8124, 65XA-8125 | 3050776 (8122), 3046109 (8123), 3046100 (8124), 3046123 (8125) | CH4 3W | OSTA 24 | 19 | 6 | AREA 6 / UNIT 19 | 620 | 622 | 2 | 4 | 2_4 | 57-19-TP620-I004-HES | WP57-19-TP620-I004-HES | 30_WP57-19-TP620-I004-HES (65XA-8122, 65XA-8123, 65XA-8124, 65XA-8125) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3050776 (8122), 3046109 (8123), 3046100 (8124), 3046123 (8125) | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-06-INC-LST-4003
31 | 65XA-8126, 65XA-8127, 65XA-8128, 65XA-8129 | 3046087 (8126), 3048807 (8127), 3046114 (8128), 3049413 (8129) | CH4 3W | OSTA 24 | 19 | 6 | AREA 6 / UNIT 19 | 620 | 622 | 2 | 4 | 2_4 | 57-19-TP620-I005-HES | WP57-19-TP620-I005-HES | 31_WP57-19-TP620-I005-HES (65XA-8126, 65XA-8127, 65XA-8128, 65XA-8129) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3046087 (8126), 3048807 (8127), 3046114 (8128), 3049413 (8129) | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-06-INC-LST-4003
32 | 65XA-8130, 65XA-8131, 65XA-8132, 65XA-8133 | 3033005 (8130), 3050769 (8131), 3046103 (8132), 3046105 (8133) | CH4 3W | OSTA 24 | 19 | 6 | AREA 6 / UNIT 19 | 620 | 622 | 2 | 4 | 2_4 | 57-19-TP620-I006-HES | WP57-19-TP620-I006-HES | 32_WP57-19-TP620-I006-HES (65XA-8130, 65XA-8131, 65XA-8132, 65XA-8133) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3033005 (8130), 3050769 (8131), 3046103 (8132), 3046105 (8133) | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-06-INC-LST-4003
33 | 65XA-8134, 65XA-8135, 65XA-8138, 65XA-8142, 65XA-8143 | 3048806 (8134), 3048817 (8135), 3048811 (8138), 3045776 (8142), 3048822 (8143) | CH4 3W | OSTA 24 | 19 | 6 | AREA 6 / UNIT 19 | 620 | 622 | 2 | 5 | 2_5 | 57-19-TP620-I007-HES | WP57-19-TP620-I007-HES | 33_WP57-19-TP620-I007-HES (65XA-8134, 65XA-8135, 65XA-8138, 65XA-8142, 65XA-8143) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3048806 (8134), 3048817 (8135), 3048811 (8138), 3045776 (8142), 3048822 (8143) | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-06-INC-LST-4003
34 | 65XA-8113, 65XA-8114 | 3048029 (8113), 3048052 (8114) | H2 3W | OSTA 24 | 19 | 6 | AREA 6 / UNIT 19 | 620 | 622 | 2 | 2 | 2_2 | 57-19-TP620-I008-HES | WP57-19-TP620-I008-HES | 34_WP57-19-TP620-I008-HES (65XA-8113, 65XA-8114) | GASENSOR | 4.8KG | HE-CT8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, low temperature catalytic bead | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CT8900 | 3048029 (8113), 3048052 (8114) | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-06-INC-LST-4003
35 | 65XA-8101, 65XA-8102, 65XA-8103, 65XA-8104 | AXGK2300196 (8101), AXGK2300186 (8102), AXGK2300187 (8103), AXGK2300189 (8104) | H2S 2W | OSTA 24 | 19 | 6 | AREA 6 / UNIT 19 | 620 | 622 | 2 | 4 | 2_4 | 57-19-TP620-I009-HES | WP57-19-TP620-I009-HES | 35_WP57-19-TP620-I009-HES (65XA-8101, 65XA-8102, 65XA-8103, 65XA-8104 ) | GASTRON | 2KG | GTD-2000TX | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | GTD-2000TX | AXGK2300196 (8101), AXGK2300186 (8102), AXGK2300187 (8103), AXGK2300189 (8104) | 0-20mA, -12.5-50 PPM | IP66 | GASTRON | RESET-EXE-HES-06-INC-LST-4003
36 | 65XA-8105, 65XA-8106, 65XA-8139, 65XA-8140, 65XA-8141 | AXGK2300192 (8105), AXGK2300193 (8106), AXGK2300195 (8139), AXGK2300185 (8140), AXGK2300191 (8141) | H2S 2W | OSTA 24 | 19 | 6 | AREA 6 / UNIT 19 | 620 | 622 | 2 | 5 | 2_5 | 57-19-TP620-I010-HES | WP57-19-TP620-I010-HES | 36_WP57-19-TP620-I010-HES (65XA-8105, 65XA-8106, 65XA-8139, 65XA-8140, 65XA-8141) | GASTRON | 2KG | GTD-2000TX | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | GTD-2000TX | AXGK2300192 (8105), AXGK2300193 (8106), AXGK2300195 (8139), AXGK2300185 (8140), AXGK2300191 (8141) | 0-20mA, -12.5-50 PPM | IP66 | GASTRON | RESET-EXE-HES-06-INC-LST-4003
37 | 65XA-8111, 65XA-8112 | 3047363 (8111), 3047367 (8112) | H2S 3W | OSTA 24 | 19 | 6 | AREA 6 / UNIT 19 | 620 | 622 | 2 | 2 | 2_2 | 57-19-TP620-I011-HES | WP57-19-TP620-I011-HES | 37_WP57-19-TP620-I011-HES (65XA-8111, 65XA-8112) | GASENSOR | 4.8KG | HE-CE8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CE8900 | 3047363 (8111), 3047367 (8112) | 0-20mA, -12.5-50 PPM | IP66 | GASENSOR | RESET-EXE-HES-06-INC-LST-4003
38 | 65H2-121 | 3048021 | H2 3W | OSTA 23 | 51 | 5A | AREA 5A / UNIT 51 | 620 | 622 | 4 | 1 | 4_1 | 57-51-TP620-I001-HES | WP57-51-TP620-I001-HES | 38_WP57-51-TP620-I001-HES (65H2-121) | GASENSOR | 4.8KG | HE-CT8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | 1Tr x 1.5mm2, 3 Cores | 500V | 51-JB-H2121 | 65H2-121 | IP66 | PHOENIX CONTACT | RESET-EXE-HES-00-MCI-MAF-4003 | Ex II 2G Ex e II T6/T5 | Area 5A / Unit 51 |  | Wall mount | Continuous diffusion, low temperature catalytic bead | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CT8900 | 3048021 | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-5A-INC-LST-4001
39 | 65H2S-129 | 3047358 | H2S 3W | OSTA 23 | 64 | 5A | AREA 5A / UNIT 64 | 620 | 622 | 4 | 1 | 4_1 | 57-64-TP620-I001-HES | WP57-64-TP620-I001-HES | 39_WP57-64-TP620-I001-HES (65H2S-129) | GASENSOR | 4.8KG | HE-CE8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | 1Tr x 1.5mm2, 3 Cores | 500V | 64-JB-H2S129 | 65H2S-129 | IP66 | PHOENIX CONTACT | RESET-EXE-HES-00-MCI-MAF-4003 | Ex II 2G Ex e II T6/T5 | Area 5A / Unit 64 |  | Wall mount | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CE8900 | 3047358 | 0-20mA, -12.5-50 PPM | IP66 | GASENSOR | RESET-EXE-HES-5A-INC-LST-4001
40 | 65H2S-128 | 3046091 | H2S 3W | OSTA 23 | 64 | 5A | AREA 5A / UNIT 64 | 620 | 622 | 2 | 1 | 2_1 | 57-64-TP620-I002-HES | WP57-64-TP620-I002-HES | 40_WP57-64-TP620-I002-HES (65H2S-128) | GASENSOR | 4.8KG | HE-CE8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CE8900 | 3046091 | 0-20mA, -12.5-50 PPM | IP66 | GASENSOR | RESET-EXE-HES-5A-INC-LST-4001
41 | 65GA-201, 65GA-270, 65GA-274 | 3048819 (201), 3049432 (270), 3050790 (274) | CH4 3W | OSTA 23 | 66 | 4A | AREA 4A / UNIT 66 | 620 | 622 | 4 | 3 | 4_3 | 57-66-TP620-I001-HES | WP57-66-TP620-I001-HES | 41_WP57-66-TP620-I001-HES (65GA-201, 65GA-270, 65GA-274) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | 1Tr x 1.5mm2, 3 Cores | 500V | 66-JB-GA201, 66-JB-GA270, 66-JB-GA274 | 65GA-201, 65GA-270, 65GA-274 | IP66 | PHOENIX CONTACT | RESET-EXE-HES-00-MCI-MAF-4003 | Ex II 2G Ex e II T6/T5 | Area 4A / Unit 66 |  | Wall mount | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3048819 (201), 3049432 (270), 3050790 (274) | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-4A-INC-LST-4001
42 | 65GA-206, 65GA-245, 65GA-246 | 3048804 (206), 3046097 (245), 3049934 (246) | CH4 3W | OSTA 23 | 71 | 4A | AREA 4A / UNIT 71 | 620 | 622 | 2 | 3 | 2_3 | 57-71-TP620-I001-HES | WP57-71-TP620-I001-HES | 42_WP57-71-TP620-I001-HES (65GA-206, 65GA-245, 65GA-246) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3048804 (206), 3046097 (245), 3049934 (246) | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-4A-INC-LST-4001
43 | 65GA-249 | 3046120 | CH4 3W | OSTA 23 | 71 | 4A | AREA 4A / UNIT 71 | 620 | 622 | 4 | 1 | 4_1 | 57-71-TP620-I002-HES | WP57-71-TP620-I002-HES | 43_WP57-71-TP620-I002-HES (65GA-249) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | 1Tr x 1.5mm2, 3 Cores | 500V | 66-JB-GA249 | 65GA-249 | IP66 | PHOENIX CONTACT | RESET-EXE-HES-00-MCI-MAF-4003 | Ex II 2G Ex e II T6/T5 | Area 4A / Unit 71 |  | Wall mount | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3046120 | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-4A-INC-LST-4001
44 | 65GA-205, 65GA-207 | 3050796 (205), 3048814 (207) | CH4 3W | OSTA 23 | 71 | 4A | AREA 4A / UNIT 71 | 620 | 622 | 2 | 2 | 2_2 | 57-71-TP620-I003-HES | WP57-71-TP620-I003-HES | 44_WP57-71-TP620-I003-HES (65GA-205, 65GA-207) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3050796 (205), 3048814 (207) | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-4A-INC-LST-4001
45 | 65GA-225, 65GA-229, 65GA-230, 65GA-231 | 3046117 (225), 3048827 (229), 3048832 (230), 3050792 (231) | CH4 3W | OSTA 23 | 73 | 4A | AREA 4A / UNIT 73 | 620 | 622 | 2 | 4 | 2_4 | 57-73-TP620-I001-HES | WP57-73-TP620-I001-HES | 45_WP57-73-TP620-I001-HES (65GA-225, 65GA-229, 65GA-230, 65GA-231) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3046117 (225), 3048827 (229), 3048832 (230), 3050792 (231) | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-4A-INC-LST-4001
46 | 65GA-232, 65GA-233, 65GA-234, 65GA-236 | 3050774 (232), 3049435 (233), 3049428 (234), 3049427 (236) | CH4 3W | OSTA 23 | 73 | 4A | AREA 4A / UNIT 73 | 620 | 622 | 2 | 4 | 2_4 | 57-73-TP620-I002-HES | WP57-73-TP620-I002-HES | 46_WP57-73-TP620-I002-HES (65GA-232, 65GA-233, 65GA-234, 65GA-236) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3050774 (232), 3049435 (233), 3049428 (234), 3049427 (236) | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-4A-INC-LST-4001
47 | 65GA-226 | 3046118 | CH4 3W | OSTA 23 | 73 | 4A | AREA 4A / UNIT 73 | 620 | 622 | 2 | 1 | 2_1 | 57-73-TP620-I003-HES | WP57-73-TP620-I003-HES | 47_WP57-73-TP620-I003-HES (65GA-226) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3046118 | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-4A-INC-LST-4001
48 | 65GA-215, 65GA-216, 65GA-220, 65GA-221, 65GA-223 | 3050762 (215), 3046077 (216), 3049439 (220), 3050809 (221), 3046104 (223) | CH4 3W | OSTA 23 | 75 | 4A | AREA 4A / UNIT 75 | 620 | 622 | 2 | 5 | 2_5 | 57-75-TP620-I001-HES | WP57-75-TP620-I001-HES | 48_WP57-75-TP620-I001-HES (65GA-215, 65GA-216, 65GA-220, 65GA-221, 65GA-223) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3050762 (215), 3046077 (216), 3049439 (220), 3050809 (221), 3046104 (223) | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-4A-INC-LST-4001
49 | 65GA-218 | 3046094 | CH4 3W | OSTA 23 | 75 | 4A | AREA 4A / UNIT 75 | 620 | 622 | 4 | 1 | 4_1 | 57-75-TP620-I002-HES | WP57-75-TP620-I002-HES | 49_WP57-75-TP620-I002-HES (65GA-218) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | 1Tr x 1.5mm2, 3 Cores | 500V | 66-JB-GA218 | 65GA-218 | IP66 | PHOENIX CONTACT | RESET-EXE-HES-00-MCI-MAF-4003 | Ex II 2G Ex e II T6/T5 | Area 4A / Unit 75 |  | Wall mount | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3046094 | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-4A-INC-LST-4001
50 | 65GA-250 | 3049416 | CH4 3W | OSTA 23 | 75 | 4A | AREA 4A / UNIT 75 | 620 | 622 | 2 | 1 | 2_1 | 57-75-TP620-I003-HES | WP57-75-TP620-I003-HES | 50_WP57-75-TP620-I003-HES (65GA-250) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3049416 | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-4A-INC-LST-4001
51 | 65GA-228 | 3049412 | CH4 3W | OSTA 23 | 75 | 4A | AREA 4A / UNIT 75 | 620 | 622 | 2 | 1 | 2_1 | 57-75-TP620-I004-HES | WP57-75-TP620-I004-HES | 51_WP57-75-TP620-I004-HES (65GA-228) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3049412 | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-4A-INC-LST-4001
52 | 65GA-240 | 3048826 | CH4 3W | OSTA 23 | 77 | 4A | AREA 4A / UNIT 77 | 620 | 622 | 2 | 1 | 2_1 | 57-77-TP620-I001-HES | WP57-77-TP620-I001-HES | 52_WP57-77-TP620-I001-HES (65GA-240) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3048826 | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-4A-INC-LST-4001
53 | 65GA-267 | 3048803 | CH4 3W | OSTA 23 | 77 | 4A | AREA 4A / UNIT 77 | 620 | 622 | 4 | 1 | 4_1 | 57-77-TP620-I002-HES | WP57-77-TP620-I002-HES | 53_WP57-77-TP620-I002-HES (65GA-267) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | 1Tr x 1.5mm2, 3 Cores | 500V | 66-JB-GA267 | 65GA-267 | IP66 | PHOENIX CONTACT | RESET-EXE-HES-00-MCI-MAF-4003 | Ex II 2G Ex e II T6/T5 | Area 4A / Unit 77 |  | Wall mount | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3048803 | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-4A-INC-LST-4001
54 | 65GA-151B, 65GA-151C | 3050781 (151B), 3050768 (151C) | CH4 3W | TA 2024 | MCB | MCB | AREA MCB / UNIT MCB | 620 | 622 | 2 | 2 | 2_2 | 57-MCB-TP620-I001-HES | WP57-MCB-TP620-I001-HES | 54_WP57-MCB-TP620-I001-HES (65GA-151B, 65GA-151C) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3050781 (151B), 3050768 (151C) | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-93-INC-LST-4003
55 | 65XA-2631, 65XA-2632, 65XA-2633 | AXGK2300210 (2631), AXGK2300211 (2632), AXGK2300212 (2633) | H2S 2W | TA 2024 | MCB | MCB | AREA MCB / UNIT MCB | 620 | 622 | 2 | 3 | 2_3 | 57-MCB-TP620-I002-HES | WP57-MCB-TP620-I002-HES | 55_WP57-MCB-TP620-I002-HES (65XA-2631, 65XA-2632, 65XA-2633) | GASTRON | 2KG | GTD-2000TX | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | GTD-2000TX | AXGK2300210 (2631), AXGK2300211 (2632), AXGK2300212 (2633) | 0-20mA, -12.5-50 PPM | IP66 | GASTRON | RESET-EXE-HES-93-INC-LST-4003
56 | 65XA-8190A, 65XA-8190B, 65XA-8190C | AXGK2300203 (8190A), AXGK2300204 (8190B), AXGK2300205 (8190C) | H2S 2W | TA 2024 | SCR8 | 6 | AREA 6 / UNIT SCR8 | 620 | 622 | 2 | 3 | 2_3 | 57-SCR8-TP620-I001-HES | WP57-SCR8-TP620-I001-HES | 56_WP57-SCR8-TP620-I001-HES (65XA-8190A, 65XA-8190B, 65XA-8190C) | GASTRON | 2KG | GTD-2000TX | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | GTD-2000TX | AXGK2300203 (8190A), AXGK2300204 (8190B), AXGK2300205 (8190C) | 0-20mA, -12.5-50 PPM | IP66 | GASTRON | RESET-EXE-HES-06-INC-LST-4003
57 | 65XA-8193A, 65XA-8193B, 65XA-8193C | 3049441 (8193A), 3049420 (8193B), 3048818 (8193C) | CH4 3W | TA 2024 | SCR8 | 6 | AREA 6 / UNIT SCR8 | 620 | 622 | 2 | 3 | 2_3 | 57-SCR8-TP620-I002-HES | WP57-SCR8-TP620-I002-HES | 57_WP57-SCR8-TP620-I002-HES (65XA-8193A, 65XA-8193B, 65XA-8193C) | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3049441 (8193A), 3049420 (8193B), 3048818 (8193C) | 0-22mA, -25-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-06-INC-LST-4003
58 | MCB-FGS-001 SYSTEM, MCB-FGS-001 MDF |  |  | TA 2024 | MCB | 1A, 1B | AREA 1A, 1B / UNIT MCB | 620 | 622 | P |  |  | 57-MCB-TP620-I003-HES | WP57-MCB-TP620-I003-HES | 58_WP57-MCB-TP620-I003-HES (MCB-FGS-001 SYSTEM, MCB-FGS-001 MDF) | [23 empty] | RESET-EXE-HES-93-INC-DWG-4001 RESET-EXE-HES-93-INC-DWG-4002 RESET-EXE-HES-93-INC-DWG-4003 RESET-EXE-HES-93-INC-LST-4001 RESET-EXE-HES-93-INC-DWG-4007
59 | OMS-FGS-001 SYSTEM, OMS-FGS-001 MDF |  |  | TA 2024 | OMS | 4A | AREA 4A / UNIT OMS | 620 | 622 | P |  |  | 57-OMS-TP620-I001-HES | WP57-OMS-TP620-I001-HES | 59_WP57-OMS-TP620-I001-HES (OMS-FGS-001 SYSTEM, OMS-FGS-001 MDF) | [23 empty] | RESET-EXE-HES-95-INC-DWG-4001 RESET-EXE-HES-95-INC-DWG-4002 RESET-EXE-HES-95-INC-DWG-4003 RESET-EXE-HES-95-INC-LST-4001 RESET-EXE-HES-95-INC-DWG-4007
60 | SS1-FGS-001 SYSTEM, SS1-FGS-001 MDF |  |  | TA 2024 | SS01 | 4A | AREA 4A / UNIT SS01 | 620 | 622 | P |  |  | 57-SS1-TP620-I001-HES | WP57-SS1-TP620-I001-HES | 60_WP57-SS1-TP620-I001-HES (SS1-FGS-001 SYSTEM, SS1-FGS-001 MDF) | [23 empty] | RESET-EXE-HES-97-INC-DWG-4001 RESET-EXE-HES-97-INC-DWG-4003 RESET-EXE-HES-97-INC-DWG-4005 RESET-EXE-HES-97-INC-LST-4001 RESET-EXE-HES-97-INC-DWG-4010
61 | SS7-FGS-001 SYSTEM, SS7-FGS-001 MDF |  |  | TA 2024 | SS07 | 4A | AREA 4A / UNIT SS07 | 620 | 622 | P |  |  | 57-SS7-TP620-I001-HES | WP57-SS7-TP620-I001-HES | 61_WP57-SS7-TP620-I001-HES (SS7-FGS-001 SYSTEM, SS7-FGS-001 MDF) | [23 empty] | RESET-EXE-HES-97-INC-DWG-4002 RESET-EXE-HES-97-INC-DWG-4004 RESET-EXE-HES-97-INC-DWG-4006 RESET-EXE-HES-97-INC-LST-4002 RESET-EXE-HES-97-INC-DWG-4011
62 | 8-FGS-001 SYSTEM, 8-FGS-002 SYSTEM, 8-MDF-001, 8-MDF-002, 8-MDF-003 |  |  | TA 2024 | SCR8 | 6 | AREA 6 / UNIT SCR8 | 620 | 622 | P |  |  | 57-SCR8-TP620-I003-HES | WP57-SCR8-TP620-I003-HES | 62_WP57-SCR8-TP620-I003-HES (8-FGS-001 SYSTEM, 8-FGS-002 SYSTEM, 8-MDF-001, 8-MDF-002, 8-MDF-003) | [23 empty] | RESET-EXE-HES-06-INC-DWG-4001 RESET-EXE-HES-06-INC-DWG-4002 RESET-EXE-HES-06-INC-DWG-4003 RESET-EXE-HES-06-INC-LST-4001 RESET-EXE-HES-06-INC-DWG-4007

## TP GA
TOC Template |  | Actual (GD) |  |  | Actual (GD)
1 | I-002 TEST PACK LIST | 1 | I-002 TEST PACK LIST |  | 1 | I-002 TEST PACK LIST
2 | I-003 TIE-IN LIST | 2 | I-003 TIE-IN LIST |  | 2 | I-003 TIE-IN LIST
3 | I-004 TEST PACK MAP | 3 | I-004 TEST PACK MAP |  | 3 | I-004 TEST PACK MAP
4 | PROJECT WORK CONTROL SHEET (PWCS) (For TA only) | 4 | PROJECT WORK CONTROL SHEET (PWCS) (For TA only) |  | 4 | PROJECT WORK CONTROL SHEET (PWCS) (For TA only)
5 | I-101 TEST PACK COMPLETION RECORD (TPCR) | 5 | I-101 TEST PACK COMPLETION RECORD (TPCR) |  | 5 | I-101 TEST PACK COMPLETION RECORD (TPCR)
6 | I-1XXA CONSTRUCTION (ITR-A) | 6 | I-111A |  | 6 | I-106A
7 | I-1XXB PRE-COMMISSIONING (ITR-B) | 7 | I-111B |  | 7 | I-106B
8 | Subsequent ITRs | 8 | I-101A |  | 8 | 1-005 PUNCH LIST REGISTER
9 | Subsequent ITRs | 9 | I-104A |  | 9 | SITE ACCPETANCE TEST REPORT
10 | 1-005 PUNCH LIST REGISTER | 10 | 1-005 PUNCH LIST REGISTER
|  | 11 | MATERIAL RECEIVING INSPECTION REPORT
|  | 12 | SITE ACCPETANCE TEST REPORT
| SUB SYSTEM AND SUB SUB WRITE AS NUMBER OR TEXT - number |  |  | formats required
| cabinet drawings - layout and cabinet dwg under test pack map |  |  | 1 gd for before and after 4 itr
| SCR8 OR MG3, DOC SCR8 - scr8 |  |  | 1 gd for before and after 2 itr (no101 and 104) and for ta include wcs
1 gd for i-106 and wcs

## Spare List
No. | S/N | GD Type | No. | Tag No. | GD Type | Unit
SN_1 | 3049436 | CH4 3W | STG_1 | 65H2S-105 | H2S 3W | 11
SN_2 | 3050766 | CH4 3W | STG_2 | 65GA-269 | CH4 3W | 66
SN_3 | 3049425 | CH4 3W | STG_3 | 65GA-204 | CH4 3W | 71
SN_4 | 3046107 | CH4 3W | STG_4 | 65GA-209 | CH4 3W | 71
SN_5 | 3048831 | CH4 3W | STG_5 | 65GA-248 | CH4 3W | 71
SN_6 | 3049424 | CH4 3W | STG_6 | 65GA-254 | CH4 3W | 73
SN_7 | 3046121 | CH4 3W | STG_7 | 65GA-257 | CH4 3W | 73
SN_8 | 3049429 | CH4 3W | STG_8 | 65GA-258 | CH4 3W | 73
SN_9 | 3048824 | CH4 3W | STG_9 | 65GA-259 | CH4 3W | 73
SN_10 | 3049411 | CH4 3W | STG_10 | 65GA-261 | CH4 3W | 73
SN_11 | 3048805 | CH4 3W | STG_11 | 65GA-262 | CH4 3W | 73
SN_12 | 3048821 | CH4 3W | STG_12 | 65GA-265 | CH4 3W | 73
SN_13 | 3049414 | CH4 3W | STG_13 | 65GA-275 | CH4 3W | 73
SN_14 | 3046108 | CH4 3W | STG_14 | 65GA-276 | CH4 3W | 73
SN_15 | 3048825 | CH4 3W | STG_15 | 65GA-217 | CH4 3W | 75
SN_16 | 3049430 | CH4 3W | STG_16 | 65GA-222 | CH4 3W | 75
SN_17 | 3049418 | CH4 3W | STG_17 | 65GA-241 | CH4 3W | 77
SN_18 | 3049438 | CH4 3W | STG_18 | 65GA-266 | CH4 3W | 77
SN_19 | 3047348 | H2S 3W | STG_19 | 65XA-8158 | H2S 2W | 18
SN_20 | 3046092 | H2S 3W | STG_20 | 65XA-8161 | H2S 2W | 18
SN_21 | AXGK2300202 | H2S 2W | STG_21 | 65XA-8163 | H2S 2W | 18
SN_22 | AXGK2300206 | H2S 2W | STG_22 | 65XA-8110 | H2S 3W | 19
SN_23 | AXGK2300207 | H2S 2W | STG_23 | 65GA-151A | CH4 3W | MCB

## Technical Details
ITEM | AREA |  | UNIT | TAG NO | S/N | DESCRIPTION | DETECTION RANGE |  |  |  | ALARM SET POINT |  |  |  | TRIP SETPOINT |  | FAULT SIGNAL | [7 empty] | GD TYPE | Wire Type | SENSOR ELEVATION (mm) | STANCHION HEIGHT (mm) | SCAFFOLD (HxWxD) (M) | SENSOR ELEVATION | GD SUPPORT |  |  |  |  | NEW STANCHION BASE | NEW TRAY (m) | NEW JB | NEW 2" U-CLAMP | NEW SECONDARY CABLE (M) | REMARKS
[7 empty] | LOW |  | HIGH |  | HI |  | HIHI |  |  |  | TX FAULT SIGNAL |  | OPTICAL FAULT |  | OPEN LOOP |  | SHORT CIRCUIT | [7 empty] | REPLACE STANCHION / MOUNTING |  |  | UNISTRUT | C- CHANNEL
[7 empty] | EU | mA | EU | mA | EU | mA | EU | mA | EU | mA | Lower mA | Upper mA | EU | mA | EU | mA | EU | mA | [6 empty] | STATUS | V | H
1 | 1A | MCB | 11 | 65GA-106 | 3048820 | CH4 IR GD P-1111A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 380 | 400 | N/A | Maintain | Yes | 0.8 |  | N/A | N/A | CONCRETE FLOOR | 1.8 | Yes | Yes | 2 | -
2 | 1A | MCB | 11 | 65GA-107 | 3046101 | CH4 IR GD P-1107A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 380 | 400 | N/A | Maintain | Yes | 0.8 |  | N/A | N/A | CONCRETE FLOOR | 0.8 | Yes | Yes | 2 | -
3 | 1A | MCB | 11 | 65GA-108 | 3046099 | CH4 IR GD P-1106A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 380 | 400 | N/A | Maintain | Yes | 0.8 |  | N/A | N/A | CONCRETE FLOOR | 0.8 | N/A | N/A | N/A | -
4 | 1A | MCB | 11 | 65GA-110 | 3046098 | CH4 IR GD P-1125A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 380 | 400 | N/A | Maintain | Yes | 0.8 |  | N/A | N/A | CONCRETE FLOOR | 1.8 | Yes | Yes | 2 | -
5 | 1A | MCB | 11 | 65GA-111 | 3050785 | CH4 IR GD P-1124A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 380 | 400 | N/A | Maintain | Yes | 0.8 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
6 | 1A | MCB | 11 | 65GA-115 | 3050804 | CH4 IR GD P-1109A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 400 | 400 | N/A | Maintain | Yes | 0.8 |  | N/A | N/A | CONCRETE FLOOR | 2.8 | Yes | Yes | 2 | -
7 | 1A | MCB | 11 | 65GA-116 | 3048810 | CH4 IR GD P-1117A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 400 | 400 | N/A | Maintain | Yes | 0.8 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
8 | 1A | MCB | 11 | 65GA-119 | 3048828 | CH4 GD P-1158A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 430 | 400 | N/A | Maintain | Yes | 0.8 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
9 | 1A | MCB | 11 | 65GA-120 | 3049423 | CH4 GD P-1125A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 430 | 400 | N/A | Maintain | Yes | 0.8 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
10 | 1A | MCB | 11 | 65GA-121 | 3050767 | CH4 GD P-1128A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 380 | 400 | N/A | Maintain | Yes | 0.8 |  | N/A | N/A | CONCRETE FLOOR | 1.8 | N/A | N/A | N/A | -
11 | 1A | MCB | 11 | 65GA-601 | AXGK2300184 | H2S GD P-1112C | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 10 | 7.2 | 3.6 | 21.5 | N/A | N/A | -3.125 | 3 | 54.6875 | 21.5 | H2S | 2-wire | 780 | 1280 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 65XA-601 AT SITE BUT 65GA-601 IN SYSTEM
12 | 1A | MCB | 11 | 65H2-120 | 3048032 | H2 GD V-1113 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | N/A | N/A | -17.1875 | 1.25 | 109.375 | 21.5 | H2 | 3-wire | 5200 | 400 | 6x2x2 | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -
13 | 1A | MCB | 11 | 65H2S-101 | 3041318 | H2S GD K-1101A/B | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 10 | 7.2 | 3.6 | 21.5 | N/A | N/A | -8.5938 | 1.25 | 54.6875 | 21.5 | H2S | 3-wire | 240 | 400 | N/A | Increase to 0.5m | Yes | 1.2 |  | N/A | N/A | GRATING | 1 | Yes | Yes | 2 | -
14 | 1A | MCB | 11 | 65H2S-102 | 3041383 | H2S GD K-1101A/B | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 10 | 7.2 | 3.6 | 21.5 | N/A | N/A | -8.5938 | 1.25 | 54.6875 | 21.5 | H2S | 3-wire | 240 | 400 | N/A | Increase to 0.5m | Yes | 1.2 |  | N/A | N/A | GRATING | 1 | Yes | Yes | 2 | -
15 | 1A | MCB | 11 | 65H2S-103 | 3046075 | H2S GD K-1101A/B | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 10 | 7.2 | 3.6 | 21.5 | N/A | N/A | -8.5938 | 1.25 | 54.6875 | 21.5 | H2S | 3-wire | 240 | 400 | N/A | Increase to 0.5m | Yes | 1.2 |  | N/A | N/A | GRATING | 1 | Yes | Yes | 2 | -
16 | 1A | MCB | 11 | 65H2S-104 | 3046084 | H2S GD K-1101A/B | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 10 | 7.2 | 3.6 | 21.5 | N/A | N/A | -8.5938 | 1.25 | 54.6875 | 21.5 | H2S | 3-wire | 240 | 400 | N/A | Increase to 0.5m | Yes | 1.2 |  | N/A | N/A | GRATING | 1 | Yes | Yes | 2 | -
17 | 1A | MCB | 11 | 65H2S-105 | EXISTING | H2S GD ST-11-A | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 10 | 7.2 | 3.6 | 21.5 | N/A | N/A | -8.5938 | 1.25 | 54.6875 | 21.5 | H2S | 3-wire | 250 | 400 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Latest info: GD replaced by Operation but not in list of replaced GD
18 | 1A | MCB | 11 | 65H2S-107 | 3047355 | H2S GD ST-11-C | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 10 | 7.2 | 3.6 | 21.5 | N/A | N/A | -8.5938 | 1.25 | 54.6875 | 21.5 | H2S | 3-wire | 240 | 400 | N/A | Increase to 0.5m | Yes | 1.2 |  | N/A | N/A | CHECKER PLATE | 2 | Yes | Yes | 2 | -
19 | 1A | MCB | 14 | 65GA-125 | 3046113 | CH4 GD K-1401A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 440 | 400 | N/A | Maintain | Yes | 0.8 |  | N/A | N/A | GRATING | 0.8 | Yes | Yes | 2 | -
20 | 1A | MCB | 14 | 65GA-126 | 3048829 | CH4 GD K-1401A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 440 | 400 | N/A | Maintain | Yes | 0.8 |  | N/A | N/A | GRATING | 0.8 | Yes | Yes | 2 | -
21 | 1A | MCB | 14 | 65GA-127 | 3049419 | CH4 GD K-1401A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 440 | 400 | N/A | Maintain | Yes | 0.8 |  | N/A | N/A | GRATING | 0.8 | Yes | Yes | 2 | -
22 | 1A | MCB | 14 | 65GA-128 | 3049437 | CH4 GD K-1401A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 440 | 400 | N/A | Maintain | Yes | 0.8 |  | N/A | N/A | GRATING | 0.8 | Yes | Yes | 2 | -
23 | 1A | MCB | 15 | 65H2S-122 | 3047392 | H2S GD E-1503 | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 10 | 7.2 | 3.6 | 21.5 | N/A | N/A | -8.5938 | 1.25 | 54.6875 | 21.5 | H2S | 3-wire | 1220 | 1400 | N/A | Maintain | Yes | 0.8 |  | N/A | N/A | CONCRETE FLOOR | 2 | N/A | N/A | N/A | -
24 | 1B | MCB | 12 | 65GA-129 | 3048816 | CH4 GD P-1204A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 380 | 450 | N/A | Maintain | Yes | 0.8 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
25 | 1B | MCB | 12 | 65H2-101 | 3048028 | H2 GD F-1201 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | N/A | N/A | -17.1875 | 1.25 | 109.375 | 21.5 | H2 | 3-wire | TBC | 450 | N/A | Maintain | Yes | 0.7 | 0.45 | N/A | N/A | CHECKER PLATE | 2 | N/A | N/A | N/A | -
26 | 1B | MCB | 12 | 65H2-103 | 3048010 | H2 GD R-1201 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | N/A | N/A | -17.1875 | 1.25 | 109.375 | 21.5 | H2 | 3-wire | TBC | 450 | N/A | Maintain | Yes | 0.7 | 0.45 | N/A | N/A | CHECKER PLATE | 2 | N/A | N/A | N/A | -
27 | 1B | MCB | 12 | 65H2-104 | 3048022 | H2 GD ST-12-A | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | N/A | N/A | -17.1875 | 1.25 | 109.375 | 21.5 | H2 | 3-wire | TBC | TBC | 6x2x2 | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -
28 | 1B | MCB | 12 | 65H2-112 | 3048033 | H2 GD K-1201A/B/C | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | N/A | N/A | -17.1875 | 1.25 | 109.375 | 21.5 | H2 | 3-wire | TBC | TBC | 15x3x3 | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -
29 | 1B | MCB | 12 | 65H2-113 | 3048017 | H2 GD K-1201A/B/C | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | N/A | N/A | -17.1875 | 1.25 | 109.375 | 21.5 | H2 | 3-wire | TBC | TBC | 15x3x3 | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -
30 | 1B | MCB | 12 | 65H2-114 | 3048030 | H2 GD K-1201A/B/C | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | N/A | N/A | -17.1875 | 1.25 | 109.375 | 21.5 | H2 | 3-wire | TBC | TBC | 15x3x3 | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -
31 | 1B | MCB | 12 | 65H2-115 | 3048020 | H2 GD V-1206 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | N/A | N/A | -17.1875 | 1.25 | 109.375 | 21.5 | H2 | 3-wire | 4335 | 4535 | 5x2x2 | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -
32 | 1B | MCB | 12 | 65H2S-111 | 3047309 | H2S GD F-1201 | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 10 | 7.2 | 3.6 | 21.5 | N/A | N/A | -8.5938 | 1.25 | 54.6875 | 21.5 | H2S | 3-wire | 330 | 450 | N/A | Increase to 0.5m | Yes | 1.2 |  | N/A | N/A | CONCRETE FLOOR | 2 | N/A | N/A | N/A | -
33 | 1B | MCB | 12 | 65H2S-114 | 3046083 | H2S GD ST-12-A | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 10 | 7.2 | 3.6 | 21.5 | N/A | N/A | -8.5938 | 1.25 | 54.6875 | 21.5 | H2S | 3-wire | 285 | 450 | N/A | Increase to 0.5m | Yes | 1.2 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
34 | 1B | MCB | 12 | 65H2S-118 | 3047395 | H2S GD K-1201A/B/C | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 10 | 7.2 | 3.6 | 21.5 | N/A | N/A | -8.5938 | 1.25 | 54.6875 | 21.5 | H2S | 3-wire | 200 | 370 | N/A | Increase to 0.5m | Yes | 1.2 |  | N/A | N/A | GRATING | 1 | Yes | Yes | 2 | -
35 | 1B | MCB | 12 | 65H2S-119 | 3046078 | H2S GD K-1201A/B/C | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 10 | 7.2 | 3.6 | 21.5 | N/A | N/A | -8.5938 | 1.25 | 54.6875 | 21.5 | H2S | 3-wire | 170 | 330 | N/A | Increase to 0.5m | Yes | 1.2 |  | N/A | N/A | GRATING | 1 | Yes | Yes | 2 | -
36 | 1B | MCB | 12 | 65H2S-120 | 3046088 | H2S GD K-1201A/B/C | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 10 | 7.2 | 3.6 | 21.5 | N/A | N/A | -8.5938 | 1.25 | 54.6875 | 21.5 | H2S | 3-wire | 200 | 370 | N/A | Increase to 0.5m | Yes | 1.2 |  | N/A | N/A | GRATING | 1 | Yes | Yes | 2 | -
37 | 1B | MCB | 13 | 65GA-132 | 3048813 | CH4 GD P-1305A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 350 | 450 | N/A | Maintain | Yes | 0.8 |  | N/A | N/A | CONCRETE FLOOR | 0.8 | Yes | Yes | 2 | -
38 | 1B | MCB | 13 | 65GA-134 | 3046115 | CH4 GD P-1301A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 400 | 450 | N/A | Maintain | Yes | 0.8 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
39 | 1B | MCB | 13 | 65GA-137 | 3048808 | CH4 GD P-1306A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 390 | 450 | N/A | Increase to 0.5m | Yes | 0.8 |  | N/A | N/A | CONCRETE FLOOR | 2.8 | Yes | Yes | 2 | -
40 | 1B | MCB | 13 | 65GA-139 | 3048830 | CH4 GD A-1308 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 390 | 450 | N/A | Maintain | Yes | 0.8 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
41 | 1B | MCB | 13 | 65GA-170 | 3050789 | CH4 GD V-1338 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 1465 | 1555 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -
42 | 1B | MCB | 13 | 65H2-106 | 3048024 | H2 GD E-1302 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | N/A | N/A | -17.1875 | 1.25 | 109.375 | 21.5 | H2 | 3-wire | TBC | 4500 | N/A | Maintain | Yes | 0.7 | 0.45 | N/A | N/A | CHECKER PLATE | 2 | Yes | Yes | 2 | -
43 | 1B | MCB | 13 | 65H2-107 | 3048053 | H2 GD ST-13-A | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | N/A | N/A | -17.1875 | 1.25 | 109.375 | 21.5 | H2 | 3-wire | 280 | 430 | N/A | Maintain | Yes | 0.8 |  | N/A | N/A | CHECKER PLATE | N/A | N/A | N/A | N/A | -
44 | 1B | MCB | 13 | 65H2-108 | 3048027 | H2 GD ST-13-A | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | N/A | N/A | -17.1875 | 1.25 | 109.375 | 21.5 | H2 | 3-wire | 265 | 450 | N/A | Maintain | Yes | 0.8 |  | N/A | N/A | GRATING | N/A | N/A | N/A | N/A | -
45 | 1B | MCB | 13 | 65H2-109 | 3048006 | H2 GD ST-13-A | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | N/A | N/A | -17.1875 | 1.25 | 109.375 | 21.5 | H2 | 3-wire | 245 | 400 | N/A | Maintain | Yes | 0.8 |  | N/A | N/A | GRATING | N/A | N/A | N/A | N/A | -
46 | 1B | MCB | 13 | 65H2-111 | 3048026 | H2 GD ST-13-A | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | N/A | N/A | -17.1875 | 1.25 | 109.375 | 21.5 | H2 | 3-wire | 310 | 450 | N/A | Maintain | Yes | 0.8 |  | N/A | N/A | CHECKER PLATE | N/A | N/A | N/A | N/A | -
47 | 1B | MCB | 13 | 65H2-116 | 3048018 | H2 GD V-1311 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | N/A | N/A | -17.1875 | 1.25 | 109.375 | 21.5 | H2 | 3-wire | TBC | 450 | N/A | Maintain | Yes | 0.7 | 0.45 | N/A | N/A | CHECKER PLATE | 2 | Yes | Yes | 2 | -
48 | 1B | MCB | 13 | 65H2-118 | 3048025 | H2 GD K-1301 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | N/A | N/A | -17.1875 | 1.25 | 109.375 | 21.5 | H2 | 3-wire | TBC | TBC | 15x2x2 | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -
49 | 4A | OMS | 66 | 65GA-201 | 3048819 | PUMP SHELTER 2 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 880 | 1000 | N/A | Maintain | Yes | 1.2 |  | N/A | N/A | CONCRETE FLOOR | 1 | Yes | Yes | 2 | -
50 | 4A | OMS | 66 | 65GA-269 | EXISTING | WATER TREATMENT | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 865 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace
51 | 4A | OMS | 66 | 65GA-270 | 3049432 | SLUG FARM | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 965 | 1000 | N/A | Maintain | Yes | 1.2 |  | N/A | 2 | CONCRETE FLOOR | 1 | Yes | Yes | 2 | New proposed GD to replace
52 | 4A | OMS | 66 | 65GA-274 | 3050790 | P.SHELTER 1 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 870 | 1000 | N/A | Maintain | Yes | 1.2 |  | N/A | N/A | CONCRETE FLOOR | 1 | Yes | Yes | 2 | New proposed GD to replace
53 | 4A | OMS | 71 | 65GA-204 | EXISTING | T-7101 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 950 | 1000 | N/A | Maintain | Yes | 1.2 |  | N/A | 2 | I-BEAM | N/A | N/A | N/A | N/A | New proposed GD to replace
54 | 4A | OMS | 71 | 65GA-205 | 3050796 | T-7102 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 990 | 1000 | N/A | Maintain | Yes | 1.2 |  | N/A | 2 | I-BEAM | N/A | N/A | N/A | N/A | New proposed GD to replace
55 | 4A | OMS | 71 | 65GA-206 | 3048804 | T-7102 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 900 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace
56 | 4A | OMS | 71 | 65GA-207 | 3048814 | T-7103 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 1030 | 1000 | N/A | Maintain | Yes | 1.2 |  | N/A | 2 | I-BEAM | N/A | N/A | N/A | N/A | New proposed GD to replace
57 | 4A | OMS | 71 | 65GA-209 | EXISTING | T-7104 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 1030 | 1000 | N/A | Maintain | Yes | 1.2 |  | N/A | 2 | I-BEAM | N/A | N/A | N/A | N/A | New proposed GD to replace
58 | 4A | OMS | 71 | 65GA-245 | 3046097 | T-7106 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 880 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace
59 | 4A | OMS | 71 | 65GA-246 | 3049934 | T-7107 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 865 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace
60 | 4A | OMS | 71 | 65GA-248 | EXISTING | T-7108 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 740 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace but already replaced to a newer model
61 | 4A | OMS | 71 | 65GA-249 | 3046120 | T-7108 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 930 | 1000 | N/A | Maintain | Yes | 1.2 |  | N/A | 2 | I-BEAM | N/A | Yes | Yes | 2 | New proposed GD to replace
62 | 4A | OMS | 73 | 65GA-225 | 3046117 | V-7301 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 900 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace
63 | 4A | OMS | 73 | 65GA-226 | 3046118 | V-7302A-D | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 950 | 1000 | N/A | Maintain | Yes | 1.2 |  | N/A | 2 | WALL MOUNT | N/A | N/A | N/A | N/A | New proposed GD to replace
64 | 4A | OMS | 73 | 65GA-229 | 3048827 | P.SHELTER 4 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 890 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace
65 | 4A | OMS | 73 | 65GA-230 | 3048832 | P.SHELTER 10 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 875 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace
66 | 4A | OMS | 73 | 65GA-231 | 3050792 | P.SHELTER 10 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 875 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace
67 | 4A | OMS | 73 | 65GA-232 | 3050774 | P.SHELTER 12 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 870 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace
68 | 4A | OMS | 73 | 65GA-233 | 3049435 | P.SHELTER 12 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 860 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace
69 | 4A | OMS | 73 | 65GA-234 | 3049428 | P.SHELTER 12 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 870 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace
70 | 4A | OMS | 73 | 65GA-236 | 3049427 | P.SHELTER 11 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 880 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace
71 | 4A | OMS | 73 | 65GA-254 | EXISTING | T-7303 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 925 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace
72 | 4A | OMS | 73 | 65GA-257 | EXISTING | T-7304 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 880 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace
73 | 4A | OMS | 73 | 65GA-258 | EXISTING | T-7305 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 915 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace but already replaced to a newer model
74 | 4A | OMS | 73 | 65GA-259 | EXISTING | T-7305 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 880 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace
75 | 4A | OMS | 73 | 65GA-261 | EXISTING | T-7306 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 920 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace but already replaced to a newer model
76 | 4A | OMS | 73 | 65GA-262 | EXISTING | T-7307 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 910 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace but already replaced to a newer model
77 | 4A | OMS | 73 | 65GA-265 | EXISTING | T-7308 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 920 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace but already replaced to a newer model
78 | 4A | OMS | 73 | 65GA-275 | EXISTING | T-7301 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 905 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace
79 | 4A | OMS | 73 | 65GA-276 | EXISTING | T-7301 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 890 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace but already replaced to a newer model
80 | 4A | SS7 | 75 | 65GA-250 | 3049416 | U75-PUMP SHELTER | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 350 | MAX 600 | N/A | Maintain | Yes | 0.8 |  | N/A | 2 | CHECKER PLATE | 1 | N/A | N/A | N/A | -
81 | 4A | OMS | 75 | 65GA-215 | 3050762 | T-7503 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 910 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace
82 | 4A | OMS | 75 | 65GA-216 | 3046077 | T-7503 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 930 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace
83 | 4A | OMS | 75 | 65GA-217 | EXISTING | T-7504 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 1000 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace but already replaced to a newer model
84 | 4A | OMS | 75 | 65GA-218 | 3046094 | T-7504 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 1000 | 1000 | N/A | Maintain | Yes | 1.2 |  | N/A | 2 | I-BEAM | N/A | YES | N/A | 2 | New proposed GD to replace
85 | 4A | OMS | 75 | 65GA-220 | 3049439 | T-7505 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 880 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace
86 | 4A | OMS | 75 | 65GA-221 | 3050809 | P.SHELTER 3A | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 880 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace
87 | 4A | OMS | 75 | 65GA-222 | EXISTING | P.SHELTER 3B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 755 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace but already replaced to a newer model
88 | 4A | OMS | 75 | 65GA-223 | 3046104 | V-7501A-D | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 900 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace
89 | 4A | OMS | 75 | 65GA-228 | 3049412 | P.SHELTER 4 U-75 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 890 | 1000 | N/A | Maintain | Yes | 1.2 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | New proposed GD to replace
90 | 4A | OMS | 77 | 65GA-240 | 3048826 | BLENDING | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 890 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace
91 | 4A | OMS | 77 | 65GA-241 | EXISTING | BLENDING | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 785 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | New proposed GD to replace
92 | 4A | OMS | 77 | 65GA-266 | EXISTING | T-7701 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 920 | 1000 | N/A | Maintain | Yes | 1.2 |  | N/A | 2 | I-BEAM | N/A | N/A | N/A | N/A | New proposed GD to replace
93 | 4A | OMS | 77 | 65GA-267 | 3048803 | T-7701 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | 950 | 1000 | N/A | Maintain | Yes | 1.2 |  | N/A | 2 | I-BEAM | N/A | Yes | N/A | 2 | New proposed GD to replace
94 | 5A | MCB | 51 | 65H2-121 | 3048021 | H2 GD V-5103 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | N/A | N/A | -17.1875 | 1.25 | 109.375 | 21.5 | H2 | 3-wire | TBC | TBC | 6x2x2 | Maintain | Yes | 1.5 |  | N/A | 2 | CHECKER PLATE | 2 | Yes | Yes | 2 | -
95 | 5A | MCB | 64 | 65H2S-128 | 3046091 | H2S GD R-6402A/B | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 10 | 7.2 | 3.6 | 21.5 | N/A | N/A | -8.5938 | 1.25 | 54.6875 | 21.5 | H2S | 3-wire | 240 | 400 | N/A | Increase to 0.5m | Yes | 1.2 |  | N/A | N/A | CONCRETE FLOOR | 1 | N/A | N/A | N/A | -
96 | 5A | MCB | 64 | 65H2S-129 | 3047358 | H2S GD V-6402 | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 10 | 7.2 | 3.6 | 21.5 | N/A | N/A | -8.5938 | 1.25 | 54.6875 | 21.5 | H2S | 3-wire | 260 | 450 | N/A | Increase to 0.5m | Yes | 1.2 |  | N/A | N/A | CHECKER PLATE | 1 | Yes | Yes | 2 | -
97 | 6 | MG3 | 18 | 65XA-8151 | AXGK2300194 | U18-E-1817A/B/C | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 15 | 8.8 | 3.6 | 21.5 | N/A | N/A | -3.125 | 3 | 54.6875 | 21.5 | H2S | 2-wire | 1200 | 1500 | N/A | Decrease to 1.0m | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | To measure sensor elevation again (1200mm)
98 | 6 | MG3 | 18 | 65XA-8152 | AXGK2300197 | U18-P-1803A/B | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 15 | 8.8 | 3.6 | 21.5 | N/A | N/A | -3.125 | 3 | 54.6875 | 21.5 | H2S | 2-wire | 730 | 1000 | N/A | Increase to 1.2m | Yes | 1.5 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
99 | 6 | MG3 | 18 | 65XA-8153 | AXGK2300188 | U18-P-1802A/B | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 15 | 8.8 | 3.6 | 21.5 | N/A | N/A | -3.125 | 3 | 54.6875 | 21.5 | H2S | 2-wire | 700 | 1000 | N/A | Increase to 1.2m | Yes | 1.5 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
100 | 6 | MG3 | 18 | 65XA-8154 | 3046116 | U18-V-1804 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | HC | 3-wire | 1160 | 1340 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -
101 | 6 | MG3 | 18 | 65XA-8155 | 3048009 | U18-V-1804 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | N/A | N/A | -17.1875 | 1.25 | 109.375 | 21.5 | H2 | 3-wire | 950 | 1340 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -
102 | 6 | MG3 | 18 | 65XA-8156 | AXGK2300190 | U18-V-1805 | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 15 | 8.8 | 3.6 | 21.5 | N/A | N/A | -3.125 | 3 | 54.6875 | 21.5 | H2S | 2-wire | 730 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -
103 | 6 | MG3 | 18 | 65XA-8157 | 3048812 | U18-F-1801 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | HC | 3-wire | 1180 | 1310 | N/A | Increase to 1.2m | Yes | 1.8 |  | N/A | N/A | CONCRETE FLOOR | 1 | N/A | N/A | N/A | To measure sensor elevation again (1180mm)
104 | 6 | MG3 | 18 | 65XA-8158 | EXISTING | U18-F-1801 | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 50 | 20 | 3.6 | 21.5 | N/A | N/A | -3.125 | 3 | 54.6875 | 21.5 | H2S | 2-wire | 760 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Latest info: GD replaced by Operation but not in list of replaced GD
105 | 6 | MG3 | 18 | 65XA-8159 | 3047997 | U18-F-1801 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | N/A | N/A | -17.1875 | 1.25 | 109.375 | 21.5 | H2 | 3-wire | 950 | 1310 | N/A | Increase to 1.2m | Yes | 1.8 |  | N/A | N/A | CONCRETE FLOOR | 1 | N/A | N/A | N/A | -
106 | 6 | MG3 | 18 | 65XA-8160 | 3050783 | U18-V-1808/P-1813 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | HC | 3-wire | 900 | 1000 | N/A | Increase to 1.2m | Yes | 1.8 |  | N/A | N/A | CONCRETE FLOOR | 1 | N/A | N/A | N/A | -
107 | 6 | MG3 | 18 | 65XA-8161 | EXISTING | U18-T-1801 | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 15 | 8.8 | 3.6 | 21.5 | N/A | N/A | -3.125 | 3 | 54.6875 | 21.5 | H2S | 2-wire | 730 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Latest info: GD replaced by Operation but not in list of replaced GD
108 | 6 | MG3 | 18 | 65XA-8162 | 3049417 | U18-P-1811A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | HC | 3-wire | 900 | 1000 | N/A | Increase to 1.2m | Yes | 1.8 |  | N/A | N/A | CONCRETE FLOOR | 1 | N/A | N/A | N/A | -
109 | 6 | MG3 | 18 | 65XA-8163 | EXISTING | U18-P-1812A/B | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 15 | 8.8 | 3.6 | 21.5 | N/A | N/A | -3.125 | 3 | 54.6875 | 21.5 | H2S | 2-wire | 730 | 1000 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Latest info: GD replaced by Operation but not in list of replaced GD
110 | 6 | MG3 | 19 | 65XA-8101 | AXGK2300196 | U19-V-1903 | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 15 | 8.8 | 3.6 | 21.5 | N/A | N/A | -3.125 | 3 | 54.6875 | 21.5 | H2S | 2-wire | 900 | 1200 | N/A | Increase to 1.2m | Yes | 1.5 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
111 | 6 | MG3 | 19 | 65XA-8102 | AXGK2300186 | U19-C-1902 | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 15 | 8.8 | 3.6 | 21.5 | N/A | N/A | -3.125 | 3 | 54.6875 | 21.5 | H2S | 2-wire | 750 | 1000 | N/A | Increase to 1.2m | Yes | 1.5 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
112 | 6 | MG3 | 19 | 65XA-8103 | AXGK2300187 | U19-P-1913A/B | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 15 | 8.8 | 3.6 | 21.5 | N/A | N/A | -3.125 | 3 | 54.6875 | 21.5 | H2S | 2-wire | 930 | 1200 | N/A | Increase to 1.2m | Yes | 1.5 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
113 | 6 | MG3 | 19 | 65XA-8104 | AXGK2300189 | U19-P-1914A/B | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 15 | 8.8 | 3.6 | 21.5 | N/A | N/A | -3.125 | 3 | 54.6875 | 21.5 | H2S | 2-wire | 930 | 1200 | N/A | Increase to 1.2m | Yes | 1.5 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
114 | 6 | MG3 | 19 | 65XA-8105 | AXGK2300192 | U19-P-1915A/B | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 15 | 8.8 | 3.6 | 21.5 | N/A | N/A | -3.125 | 3 | 54.6875 | 21.5 | H2S | 2-wire | 960 | 1200 | N/A | Increase to 1.2m | Yes | 1.5 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
115 | 6 | MG3 | 19 | 65XA-8106 | AXGK2300193 | U19-V-1907 | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 15 | 8.8 | 3.6 | 21.5 | N/A | N/A | -3.125 | 3 | 54.6875 | 21.5 | H2S | 2-wire | 960 | 1200 | N/A | Increase to 1.2m | Yes | 1.5 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
116 | 6 | MG3 | 19 | 65XA-8110 | EXISTING | U19-V-1904/1905 | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 50 | 20 | 3.6 | 21.5 | N/A | N/A | -8.5938 | 1.25 | 54.6875 | 21.5 | H2S | 3-wire | 2565 | 2500 | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | To measure sensor elevation again (2565mm) Latest info: GD replaced by Operation but not in list of replaced GD
117 | 6 | MG3 | 19 | 65XA-8111 | 3047363 | U19-K-1901A | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 50 | 20 | 3.6 | 21.5 | N/A | N/A | -8.5938 | 1.25 | 54.6875 | 21.5 | H2S | 3-wire | 520 | 1000 | N/A | Increase to 1.2m | Yes | 1.5 |  | N/A | N/A | GRATING | N/A | N/A | N/A | N/A | To measure sensor elevation again (520m)
118 | 6 | MG3 | 19 | 65XA-8112 | 3047367 | U19-K-1901B | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 50 | 20 | 3.6 | 21.5 | N/A | N/A | -8.5938 | 1.25 | 54.6875 | 21.5 | H2S | 3-wire | 620 | 1000 | N/A | Increase to 1.2m | Yes | 1.5 |  | N/A | N/A | GRATING | N/A | N/A | N/A | N/A | -
119 | 6 | MG3 | 19 | 65XA-8113 | 3048029 | U19-ANALYSER HOUSE | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | N/A | N/A | -17.1875 | 1.25 | 109.375 | 21.5 | H2 | 3-wire | 1840 | N/A | N/A | Maintain | Yes |  |  | 2 | N/A | WALL MOUNT | N/A | N/A | N/A | N/A | -
120 | 6 | MG3 | 19 | 65XA-8114 | 3048052 | U19-ANALYSER HOUSE | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | N/A | N/A | -17.1875 | 1.25 | 109.375 | 21.5 | H2 | 3-wire | 1840 | N/A | N/A | Maintain | Yes |  |  | 2 | N/A | WALL MOUNT | N/A | N/A | N/A | N/A | -
121 | 6 | MG3 | 19 | 65XA-8115 | 3049440 | U19-ANALYSER HOUSE | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | HC | 3-wire | 770 | N/A | N/A | Maintain | Yes |  |  | 2 | N/A | WALL MOUNT | N/A | N/A | N/A | N/A | -
122 | 6 | MG3 | 19 | 65XA-8116 | 3049426 | U19-ANALYSER HOUSE | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | HC | 3-wire | 770 | N/A | N/A | Maintain | Yes |  |  | 2 | N/A | WALL MOUNT | N/A | N/A | N/A | N/A | -
123 | 6 | MG3 | 19 | 65XA-8120 | 3046110 | U19-P-1902A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | HC | 3-wire | 850 | 1000 | N/A | Increase to 1.2m | Yes | 1.2 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
124 | 6 | MG3 | 19 | 65XA-8121 | 3046111 | U19-P-1903A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | HC | 3-wire | 900 | 1000 | N/A | Increase to 1.2m | Yes | 1.2 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
125 | 6 | MG3 | 19 | 65XA-8122 | 3050776 | U19-P-1917A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | HC | 3-wire | 900 | 1000 | N/A | Increase to 1.2m | Yes | 1.2 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
126 | 6 | MG3 | 19 | 65XA-8123 | 3046109 | U19-C-1904 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | HC | 3-wire | 850 | 1000 | N/A | Increase to 1.2m | Yes | 1.2 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
127 | 6 | MG3 | 19 | 65XA-8124 | 3046100 | U19-P-1904A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | HC | 3-wire | 900 | 1000 | N/A | Increase to 1.2m | Yes | 1.2 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
128 | 6 | MG3 | 19 | 65XA-8125 | 3046123 | U19-P-1905A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | HC | 3-wire | 900 | 1000 | N/A | Increase to 1.2m | Yes | 1.2 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
129 | 6 | MG3 | 19 | 65XA-8126 | 3046087 | U19-P-1906A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | HC | 3-wire | 900 | 1000 | N/A | Increase to 1.2m | Yes | 1.2 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
130 | 6 | MG3 | 19 | 65XA-8127 | 3048807 | U19-P-1907A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | HC | 3-wire | 900 | 1000 | N/A | Increase to 1.2m | Yes | 1.2 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
131 | 6 | MG3 | 19 | 65XA-8128 | 3046114 | U19-F-1901 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | HC | 3-wire | 900 | 1000 | N/A | Increase to 1.2m | Yes | 1.2 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
132 | 6 | MG3 | 19 | 65XA-8129 | 3049413 | U19-F-1902 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | HC | 3-wire | 900 | 1000 | N/A | Increase to 1.2m | Yes | 1.2 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
133 | 6 | MG3 | 19 | 65XA-8130 | 3033005 | U19-R-1901 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | HC | 3-wire | 880 | 1000 | N/A | Increase to 1.2m | Yes | 1.2 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
134 | 6 | MG3 | 19 | 65XA-8131 | 3050769 | U19-R-1902 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | HC | 3-wire | 800 | 1000 | N/A | Increase to 1.2m | Yes | 1.2 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | To measure sensor elevation again (800mm)
135 | 6 | MG3 | 19 | 65XA-8132 | 3046103 | U19-R-1903 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | HC | 3-wire | 880 | 1000 | N/A | Increase to 1.2m | Yes | 1.2 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
136 | 6 | MG3 | 19 | 65XA-8133 | 3046105 | U19-C-1901 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | HC | 3-wire | 900 | 1000 | N/A | Increase to 1.2m | Yes | 1.2 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
137 | 6 | MG3 | 19 | 65XA-8134 | 3048806 | U19-E-1903A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | HC | 3-wire | 900 | 1000 | N/A | Increase to 1.2m | Yes | 1.2 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
138 | 6 | MG3 | 19 | 65XA-8135 | 3048817 | U19-E-1902 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | HC | 3-wire | 880 | 1000 | N/A | Increase to 1.2m | Yes | 1.2 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | To measure sensor elevation again (880mm)
139 | 6 | MG3 | 19 | 65XA-8136 | 3050787 | U19-E-1905A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | HC | 3-wire | 920 | 1000 | N/A | Increase to 1.2m | Yes | 1.2 |  | N/A | N/A | CONCRETE FLOOR | 1 | N/A | N/A | N/A | -
140 | 6 | MG3 | 19 | 65XA-8137 | 3046095 | U19-E-1903C/D | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | HC | 3-wire | 910 | 1000 | N/A | Increase to 1.2m | Yes | 1.2 |  | N/A | N/A | CONCRETE FLOOR | 1 | N/A | N/A | N/A | -
141 | 6 | MG3 | 19 | 65XA-8138 | 3048811 | U19-E-1904A/B | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | HC | 3-wire | 900 | 1000 | N/A | Increase to 1.2m | Yes | 1.2 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | To measure sensor elevation again (900mm)
142 | 6 | MG3 | 19 | 65XA-8139 | AXGK2300195 | U19-C-1905/06 | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 15 | 8.8 | 3.6 | 21.5 | N/A | N/A | -3.125 | 3 | 54.6875 | 21.5 | H2S | 2-wire | 950 | 1200 | N/A | Increase to 1.2m | Yes | 1.5 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
143 | 6 | MG3 | 19 | 65XA-8140 | AXGK2300185 | U19-T-1901 | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 15 | 8.8 | 3.6 | 21.5 | N/A | N/A | -3.125 | 3 | 54.6875 | 21.5 | H2S | 2-wire | 950 | 1200 | N/A | Increase to 1.2m | Yes | 1.5 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
144 | 6 | MG3 | 19 | 65XA-8141 | AXGK2300191 | U19-V-1909/10 | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 15 | 8.8 | 3.6 | 21.5 | N/A | N/A | -3.125 | 3 | 54.6875 | 21.5 | H2S | 2-wire | 950 | 1200 | N/A | Increase to 1.2m | Yes | 1.5 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
145 | 6 | MG3 | 19 | 65XA-8142 | 3045776 | U19-V-1911 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | HC | 3-wire | 880 | 1000 | N/A | Increase to 1.2m | Yes | 1.2 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | -
146 | 6 | MG3 | 19 | 65XA-8143 | 3048822 | U19-V-1912 | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | HC | 3-wire | 900 | 1000 | N/A | Increase to 1.2m | Yes | 1.2 |  | N/A | N/A | CONCRETE FLOOR | N/A | N/A | N/A | N/A | To measure sensor elevation again (900mm)
147 | 6 | MG3 | 19 | 65XA-8144 | 3050764 | U19-ANALYSER HOUSE | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | TBC | TBC | 3x2x2 | Maintain | Yes |  |  | N/A | N/A | DUCT MOUNT | N/A | N/A | N/A | N/A | -
148 | 6 | MG3 | MG3 | 65XA-8190A | AXGK2300203 | SCR-8 H2S HVAC RM | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 15 | 8.8 | 3.6 | 21.5 | N/A | N/A | -3.125 | 3 | 54.6875 | 21.5 | H2S | 2-wire | N/A | N/A | N/A | Maintain | Yes |  |  | N/A | N/A | DUCT MOUNT | N/A | N/A | N/A | N/A | -
149 | 6 | MG3 | MG3 | 65XA-8190B | AXGK2300204 | SCR-8 H2S HVAC RM | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 15 | 8.8 | 3.6 | 21.5 | N/A | N/A | -3.125 | 3 | 54.6875 | 21.5 | H2S | 2-wire | N/A | N/A | N/A | Maintain | Yes |  |  | N/A | N/A | DUCT MOUNT | N/A | N/A | N/A | N/A | -
150 | 6 | MG3 | MG3 | 65XA-8190C | AXGK2300205 | SCR-8 H2S HVAC RM | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 15 | 8.8 | 3.6 | 21.5 | N/A | N/A | -3.125 | 3 | 54.6875 | 21.5 | H2S | 2-wire | N/A | N/A | N/A | Maintain | Yes |  |  | N/A | N/A | DUCT MOUNT | N/A | N/A | N/A | N/A | -
151 | 6 | MG3 | MG3 | 65XA-8193A | 3049441 | SCR-8 HC HVAC RM | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | N/A | N/A | N/A | Maintain | Yes |  |  | N/A | N/A | DUCT MOUNT | N/A | N/A | N/A | N/A | -
152 | 6 | MG3 | MG3 | 65XA-8193B | 3049420 | SCR-8 HC HVAC RM | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | N/A | N/A | N/A | Maintain | Yes |  |  | N/A | N/A | DUCT MOUNT | N/A | N/A | N/A | N/A | -
153 | 6 | MG3 | MG3 | 65XA-8193C | 3048818 | SCR-8 HC HVAC RM | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 50 | 12 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | N/A | N/A | N/A | Maintain | Yes |  |  | N/A | N/A | DUCT MOUNT | N/A | N/A | N/A | N/A | -
154 | MCB | MCB | MCB | 65GA-151A | EXISTING | CH4 GD MCB AIR INTA | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | N/A | N/A | N/A | Maintain | No |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Latest info: GD replaced by Operation but not in list of replaced GD
155 | MCB | MCB | MCB | 65GA-151B | 3050781 | CH4 GD MCB AIR INTA | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | N/A | N/A | 6x2x2 | Maintain | Yes |  |  | N/A | N/A | DUCT MOUNT | N/A | N/A | N/A | N/A | -
156 | MCB | MCB | MCB | 65GA-151C | 3050768 | CH4 GD MCB AIR INTA | -25 | 0 | 100 | 20 | 25 | 8 | 50 | 12 | 25 | 8 | 3.6 | 21.5 | -12.5 | 2 | -17.1875 | 1.25 | 109.375 | 21.5 | CH4 | 3-wire | N/A | N/A | 6x2x2 | Maintain | Yes |  |  | N/A | N/A | DUCT MOUNT | N/A | N/A | N/A | N/A | -
157 | MCB | MCB | MCB | 65XA-2631 | AXGK2300210 | H2S GD MCB AIR INTA | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 10 | 7.2 | 3.6 | 21.5 | N/A | N/A | -3.125 | 3 | 54.6875 | 21.5 | H2S | 2-wire | N/A | N/A | 6x2x2 | Maintain | Yes |  |  | N/A | N/A | DUCT MOUNT | N/A | N/A | N/A | N/A | -
158 | MCB | MCB | MCB | 65XA-2632 | AXGK2300211 | H2S GD MCB AIR INTA | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 10 | 7.2 | 3.6 | 21.5 | N/A | N/A | -3.125 | 3 | 54.6875 | 21.5 | H2S | 2-wire | N/A | N/A | 6x2x2 | Maintain | Yes |  |  | N/A | N/A | DUCT MOUNT | N/A | N/A | N/A | N/A | -
159 | MCB | MCB | MCB | 65XA-2633 | AXGK2300212 | H2S GD MCB AIR INTA | -12.5 | 0 | 50 | 20 | 10 | 7.2 | 15 | 8.8 | 10 | 7.2 | 3.6 | 21.5 | N/A | N/A | -3.125 | 3 | 54.6875 | 21.5 | H2S | 2-wire | N/A | N/A | 6x2x2 | Maintain | Yes |  |  | N/A | N/A | DUCT MOUNT | N/A | N/A | N/A | N/A | -

## Work Summary
AREA | UNIT | BASE TYPE |  | INT JB | C-CHANNEL | GD-COUNT
1A | 11 | CHECKER PLATE | 1 | 9 | 0 | 17
|  | CONCRETE FLOOR | 10
|  | DUCT MOUNT | 0
|  | GRATING | 4
|  | I-BEAM | 0
|  | WALL MOUNT | 0
| 14 | CHECKER PLATE | 0 | 4 | 0 | 4
|  | CONCRETE FLOOR | 0
|  | DUCT MOUNT | 0
|  | GRATING | 4
|  | I-BEAM | 0
|  | WALL MOUNT | 0
| 15 | CHECKER PLATE | 0 | 0 | 0 | 1
|  | CONCRETE FLOOR | 1
|  | DUCT MOUNT | 0
|  | GRATING | 0
|  | I-BEAM | 0
|  | WALL MOUNT | 0
1B | 12 | CHECKER PLATE | 2 | 3 | 0 | 13
|  | CONCRETE FLOOR | 3
|  | DUCT MOUNT | 0
|  | GRATING | 3
|  | I-BEAM | 0
|  | WALL MOUNT | 0
| 13 | CHECKER PLATE | 4 | 4 | 0 | 12
|  | CONCRETE FLOOR | 4
|  | DUCT MOUNT | 0
|  | GRATING | 2
|  | I-BEAM | 0
|  | WALL MOUNT | 0
4A | 66 | CHECKER PLATE | 0 | 3 | 1 | 3
|  | CONCRETE FLOOR | 3
|  | DUCT MOUNT | 0
|  | GRATING | 0
|  | I-BEAM | 0
|  | WALL MOUNT | 0
| 71 | CHECKER PLATE | 0 | 1 | 5 | 6
|  | CONCRETE FLOOR | 0
|  | DUCT MOUNT | 0
|  | GRATING | 0
|  | I-BEAM | 5
|  | WALL MOUNT | 0
| 73 | CHECKER PLATE | 0 | 0 | 1 | 9
|  | CONCRETE FLOOR | 0
|  | DUCT MOUNT | 0
|  | GRATING | 0
|  | I-BEAM | 0
|  | WALL MOUNT | 1
| 75 | CHECKER PLATE | 1 | 1 | 2 | 8
|  | CONCRETE FLOOR | 1
|  | DUCT MOUNT | 0
|  | GRATING | 0
|  | I-BEAM | 1
|  | WALL MOUNT | 0
| 77 | CHECKER PLATE | 0 | 1 | 2 | 2
|  | CONCRETE FLOOR | 0
|  | DUCT MOUNT | 0
|  | GRATING | 0
|  | I-BEAM | 2
|  | WALL MOUNT | 0
5A | 51 | CHECKER PLATE | 1 | 1 | 1 | 1
|  | CONCRETE FLOOR | 0
|  | DUCT MOUNT | 0
|  | GRATING | 0
|  | I-BEAM | 0
|  | WALL MOUNT | 0
| 64 | CHECKER PLATE | 1 | 1 | 0 | 2
|  | CONCRETE FLOOR | 1
|  | DUCT MOUNT | 0
|  | GRATING | 0
|  | I-BEAM | 0
|  | WALL MOUNT | 0
6 | 18 | CHECKER PLATE | 0 | 0 | 0 | 10
|  | CONCRETE FLOOR | 6
|  | DUCT MOUNT | 0
|  | GRATING | 0
|  | I-BEAM | 0
|  | WALL MOUNT | 0
| 19 | CHECKER PLATE | 0 | 0 | 0 | 37
|  | CONCRETE FLOOR | 30
|  | DUCT MOUNT | 1
|  | GRATING | 2
|  | I-BEAM | 0
|  | WALL MOUNT | 4
| MG3 | CHECKER PLATE | 0 | 0 | 0 | 6
|  | CONCRETE FLOOR | 0
|  | DUCT MOUNT | 6
|  | GRATING | 0
|  | I-BEAM | 0
|  | WALL MOUNT | 0
MCB | MCB | CHECKER PLATE | 0 | 0 | 0 | 5
|  | CONCRETE FLOOR | 0
|  | DUCT MOUNT | 5
|  | GRATING | 0
|  | I-BEAM | 0
|  | WALL MOUNT | 0
TOTAL |  | CHECKER PLATE | 10 | 28 | 12 | 136
|  | CONCRETE FLOOR | 59
|  | DUCT MOUNT | 12
|  | GRATING | 15
|  | I-BEAM | 8
|  | WALL MOUNT | 5

## (INFO) MRC Guideline
No. | Cluster | Area | Unit | System | Subsystem | Sub-Subsystem | ACE | Test Pack | Discipline | Package No (PN/WP) | Scope Of Work | Tag No. / Line No | Package | Contractor | Window | QC PACK Completion | Line Check | Total Punch A Open | Total Punch A Closed | Total Punch B Open | Total Punch B Closed | Total Punch C Open | Total Punch C Closed | HT/ Leak Test Completion (Mech/Piping) | Loop Test/ Function Test (E&I) | ITR A Completion (Date) | ITR A Completion | ITR B Completion (Date) | ITR B Completion | WCS (Date) | WCS | TPCR | TPCR | Remarks | x
1 | 1 | 4B | 81 | 100 | 120 | 322 | ACE 1 | WP121-81-TP121-P002-DOM | Piping | WP121 | Main Trestle And Berth Trestle Piping Replacement | 8-P81014-A2A1 LPG V | RESET | Dominant | SD 2024 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | N/A |  | 0 |  | 0 |  | 0 |  | 0 |  | x
2 | 1 | [5 empty] | #N/A |  | Mechanical | WP112 | Pilot & Ignition Line A-6401 (Upgrade Of Pilot & Ignition Line) |  | RESET | Hyperwave/Dominant | SD 2024 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | N/A |  | 0 |  | 0 |  | 0 |  | 0 |  | x
3 | 1 | [5 empty] | #N/A |  |  |  | Relief Valve Strategy and Sparing Initiatives Tie in Works / RIVAL Project |  | PCDM |  | SD 2024 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | N/A |  |  | 0 |  | 0 |  | 0 |  | 0 |  | x
4 | 1 | [5 empty] | #N/A |  |  |  | Relief Valve Strategy and Sparing Initiatives Tie in Works / RIVAL Project |  | PCDM |  | SD 2024 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | N/A |  |  | 0 |  | 0 |  | 0 |  | 0 |  | x
x |  | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
[30 empty] | ` | `
Note on C2: M Hafiz Zainal Abidin: Please fillu up all the necessary information e.g. Area, Unit, System, Sub-system and Sub-Subsystem (if applicable)
Note on I2: M Hafiz Zainal Abidin: Please assigned correct numbering for each test pack accordance to Turnover Procedure which been briefed previously
Note on K2: M Hafiz Zainal Abidin: Kindly mention your Package No.
Note on M2: M Hafiz Zainal Abidin: Please inser equipment tag no. or Line no. which within the Tes Pack Boundary
Note on N2: M Hafiz Zainal Abidin: Please choose the option "RESET or "PCDM"
Note on O2: M Hafiz Zainal Abidin: Spell out the name of Contractor
Note on P2: M Hafiz Zainal Abidin: Please choose for each test pack's window either during TA 2024 or Pre-TA 2024
Note on A5: M Hafiz Zainal Abidin: For next Test Pack, please copy the whole row and past at below new row.

## Master (GD)_BU
Internal | [9 empty] | A |  | B | C |  |  |  | D | E
Internal | [9 empty] | 28 | 136 | 28 | 6 | 5 | 136 | 136 | 39 | 106 | 14
Internal | [9 empty] | 101A | Inc in 111 | 104A | 105A | 106A | 111A | 111B | Inc in 111 | Inc in 111 | HSE
Sorted No. | Init No. | Tag No. | S/N | GD TYPE | WINDOW | WP | UNIT | AREA | SUBSYSTEM | Instrument cable (101A) | Calibration (103A) | Junction box (104A) | Instrument tubing (105A) | Elec Panel (106A) | FG Device (111A) | FG Device (111B) | Cable Tray ladder (112A) | Stanchion | Scaffold | Common ITR | internal Grouping | Test Pack Numbering
1 | 1 | 65GA-106 | 3048820 | CH4 3W | 1_Before TA | 57 | 11 | 1A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | A1 | 57-11-TP620-I001-HES
2 | 2 | 65GA-107 | 3046101 | CH4 3W | 1_Before TA | 57 | 11 | 1A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | A1 | 57-11-TP620-I001-HES
3 | 4 | 65GA-110 | 3046098 | CH4 3W | 1_Before TA | 57 | 11 | 1A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | A1 | 57-11-TP620-I001-HES
4 | 6 | 65GA-115 | 3050804 | CH4 3W | 1_Before TA | 57 | 11 | 1A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | A1 | 57-11-TP620-I001-HES
5 | 3 | 65GA-108 | 3046099 | CH4 3W | 1_Before TA | 57 | 11 | 1A | 620 |  | Y |  |  |  | Y | Y | Y | Y |  | DE | A2 | 57-11-TP620-I002-HES
6 | 10 | 65GA-121 | 3050767 | CH4 3W | 1_Before TA | 57 | 11 | 1A | 620 |  | Y |  |  |  | Y | Y | Y | Y |  | DE | A2 | 57-11-TP620-I002-HES
7 | 5 | 65GA-111 | 3050785 | CH4 3W | 1_Before TA | 57 | 11 | 1A | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | A3 | 57-11-TP620-I003-HES
8 | 7 | 65GA-116 | 3048810 | CH4 3W | 1_Before TA | 57 | 11 | 1A | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | A3 | 57-11-TP620-I003-HES
9 | 8 | 65GA-119 | 3048828 | CH4 3W | 1_Before TA | 57 | 11 | 1A | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | A3 | 57-11-TP620-I003-HES
10 | 9 | 65GA-120 | 3049423 | CH4 3W | 1_Before TA | 57 | 11 | 1A | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | A3 | 57-11-TP620-I003-HES
11 | 66 | 65H2-120 | 3048032 | H2 3W | 1_Before TA | 57 | 11 | 1A | 620 |  | Y |  |  |  | Y | Y |  |  | Y |  | A4 | 57-11-TP620-I004-HES
12 | 51 | 65GA-601 | AXGK2300184 | H2S 2W | 1_Before TA | 57 | 11 | 1A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | A5 | 57-11-TP620-I005-HES
13 | 68 | 65H2S-101 | 3041318 | H2S 3W | 1_Before TA | 57 | 11 | 1A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | A6 | 57-11-TP620-I006-HES
14 | 69 | 65H2S-102 | 3041383 | H2S 3W | 1_Before TA | 57 | 11 | 1A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | A6 | 57-11-TP620-I006-HES
15 | 70 | 65H2S-103 | 3046075 | H2S 3W | 1_Before TA | 57 | 11 | 1A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | A6 | 57-11-TP620-I006-HES
16 | 71 | 65H2S-104 | 3046084 | H2S 3W | 1_Before TA | 57 | 11 | 1A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | A6 | 57-11-TP620-I006-HES
17 | 72 | 65H2S-107 | 3047355 | H2S 3W | 1_Before TA | 57 | 11 | 1A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | A6 | 57-11-TP620-I006-HES
18 | 15 | 65GA-129 | 3048816 | CH4 3W | 1_Before TA | 57 | 12 | 1B | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | B1 | 57-12-TP620-I001-HES
19 | 54 | 65H2-104 | 3048022 | H2 3W | 1_Before TA | 57 | 12 | 1B | 620 |  | Y |  |  |  | Y | Y |  |  | Y |  | B2 | 57-12-TP620-I002-HES
20 | 60 | 65H2-112 | 3048033 | H2 3W | 1_Before TA | 57 | 12 | 1B | 620 |  | Y |  |  |  | Y | Y |  |  | Y |  | B2 | 57-12-TP620-I002-HES
21 | 61 | 65H2-113 | 3048017 | H2 3W | 1_Before TA | 57 | 12 | 1B | 620 |  | Y |  |  |  | Y | Y |  |  | Y |  | B2 | 57-12-TP620-I002-HES
22 | 62 | 65H2-114 | 3048030 | H2 3W | 1_Before TA | 57 | 12 | 1B | 620 |  | Y |  |  |  | Y | Y |  |  | Y |  | B2 | 57-12-TP620-I002-HES
23 | 63 | 65H2-115 | 3048020 | H2 3W | 1_Before TA | 57 | 12 | 1B | 620 |  | Y |  |  |  | Y | Y |  |  | Y |  | B2 | 57-12-TP620-I002-HES
24 | 52 | 65H2-101 | 3048028 | H2 3W | 1_Before TA | 57 | 12 | 1B | 620 |  | Y |  |  |  | Y | Y | Y | Y |  | DE | B3 | 57-12-TP620-I003-HES
25 | 53 | 65H2-103 | 3048010 | H2 3W | 1_Before TA | 57 | 12 | 1B | 620 |  | Y |  |  |  | Y | Y | Y | Y |  | DE | B3 | 57-12-TP620-I003-HES
26 | 75 | 65H2S-118 | 3047395 | H2S 3W | 1_Before TA | 57 | 12 | 1B | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | B4 | 57-12-TP620-I004-HES
27 | 76 | 65H2S-119 | 3046078 | H2S 3W | 1_Before TA | 57 | 12 | 1B | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | B4 | 57-12-TP620-I004-HES
28 | 77 | 65H2S-120 | 3046088 | H2S 3W | 1_Before TA | 57 | 12 | 1B | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | B4 | 57-12-TP620-I004-HES
29 | 73 | 65H2S-111 | 3047309 | H2S 3W | 1_Before TA | 57 | 12 | 1B | 620 |  | Y |  |  |  | Y | Y | Y | Y |  | DE | B5 | 57-12-TP620-I005-HES
30 | 74 | 65H2S-114 | 3046083 | H2S 3W | 1_Before TA | 57 | 12 | 1B | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | B6 | 57-12-TP620-I006-HES
31 | 22 | 65GA-170 | 3050789 | CH4 3W | 1_Before TA | 57 | 13 | 1B | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | C1 | 57-13-TP620-I001-HES
32 | 16 | 65GA-132 | 3048813 | CH4 3W | 1_Before TA | 57 | 13 | 1B | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | C2 | 57-13-TP620-I002-HES
33 | 18 | 65GA-137 | 3048808 | CH4 3W | 1_Before TA | 57 | 13 | 1B | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | C2 | 57-13-TP620-I002-HES
34 | 17 | 65GA-134 | 3046115 | CH4 3W | 1_Before TA | 57 | 13 | 1B | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | C3 | 57-13-TP620-I003-HES
35 | 19 | 65GA-139 | 3048830 | CH4 3W | 1_Before TA | 57 | 13 | 1B | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | C3 | 57-13-TP620-I003-HES
36 | 65 | 65H2-118 | 3048025 | H2 3W | 1_Before TA | 57 | 13 | 1B | 620 |  | Y |  |  |  | Y | Y |  |  | Y |  | C4 | 57-13-TP620-I004-HES
37 | 55 | 65H2-106 | 3048024 | H2 3W | 1_Before TA | 57 | 13 | 1B | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | C5 | 57-13-TP620-I005-HES
38 | 64 | 65H2-116 | 3048018 | H2 3W | 1_Before TA | 57 | 13 | 1B | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | C5 | 57-13-TP620-I005-HES
39 | 56 | 65H2-107 | 3048053 | H2 3W | 1_Before TA | 57 | 13 | 1B | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | C6 | 57-13-TP620-I006-HES
40 | 57 | 65H2-108 | 3048027 | H2 3W | 1_Before TA | 57 | 13 | 1B | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | C6 | 57-13-TP620-I006-HES
41 | 58 | 65H2-109 | 3048006 | H2 3W | 1_Before TA | 57 | 13 | 1B | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | C6 | 57-13-TP620-I006-HES
42 | 59 | 65H2-111 | 3048026 | H2 3W | 1_Before TA | 57 | 13 | 1B | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | C6 | 57-13-TP620-I006-HES
43 | 11 | 65GA-125 | 3046113 | CH4 3W | 1_Before TA | 57 | 14 | 1A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | D | 57-14-TP620-I001-HES
44 | 12 | 65GA-126 | 3048829 | CH4 3W | 1_Before TA | 57 | 14 | 1A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | D | 57-14-TP620-I001-HES
45 | 13 | 65GA-127 | 3049419 | CH4 3W | 1_Before TA | 57 | 14 | 1A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | D | 57-14-TP620-I001-HES
46 | 14 | 65GA-128 | 3049437 | CH4 3W | 1_Before TA | 57 | 14 | 1A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | D | 57-14-TP620-I001-HES
47 | 78 | 65H2S-122 | 3047392 | H2S 3W | 1_Before TA | 57 | 15 | 1A | 620 |  | Y |  |  |  | Y | Y | Y | Y |  | DE | E | 57-15-TP620-I001-HES
48 | 124 | 65XA-8154 | 3046116 | CH4 3W | 3_After TA | 57 | 18 | 6 | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | F1 | 57-18-TP620-I001-HES
49 | 127 | 65XA-8157 | 3048812 | CH4 3W | 3_After TA | 57 | 18 | 6 | 620 |  | Y |  |  |  | Y | Y | Y | Y |  | DE | F2 | 57-18-TP620-I002-HES
50 | 129 | 65XA-8160 | 3050783 | CH4 3W | 3_After TA | 57 | 18 | 6 | 620 |  | Y |  |  |  | Y | Y | Y | Y |  | DE | F2 | 57-18-TP620-I002-HES
51 | 130 | 65XA-8162 | 3049417 | CH4 3W | 3_After TA | 57 | 18 | 6 | 620 |  | Y |  |  |  | Y | Y | Y | Y |  | DE | F2 | 57-18-TP620-I002-HES
52 | 125 | 65XA-8155 | 3048009 | H2 3W | 3_After TA | 57 | 18 | 6 | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | F3 | 57-18-TP620-I003-HES
53 | 128 | 65XA-8159 | 3047997 | H2 3W | 3_After TA | 57 | 18 | 6 | 620 |  | Y |  |  |  | Y | Y | Y | Y |  | DE | F4 | 57-18-TP620-I004-HES
54 | 121 | 65XA-8151 | AXGK2300194 | H2S 2W | 3_After TA | 57 | 18 | 6 | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | F5 | 57-18-TP620-I005-HES
55 | 126 | 65XA-8156 | AXGK2300190 | H2S 2W | 3_After TA | 57 | 18 | 6 | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | F5 | 57-18-TP620-I005-HES
56 | 122 | 65XA-8152 | AXGK2300197 | H2S 2W | 3_After TA | 57 | 18 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | F6 | 57-18-TP620-I006-HES
57 | 123 | 65XA-8153 | AXGK2300188 | H2S 2W | 3_After TA | 57 | 18 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | F6 | 57-18-TP620-I006-HES
58 | 120 | 65XA-8144 | 3050764 | CH4 3W | 2_TA | 57 | 19 | 6 | 620 |  | Y |  | Y |  | Y | Y |  | Y | Y | CE | G1 | 57-19-TP620-I001-HES
59 | 112 | 65XA-8136 | 3050787 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y | Y | Y |  | DE | G2 | 57-19-TP620-I002-HES
60 | 113 | 65XA-8137 | 3046095 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y | Y | Y |  | DE | G2 | 57-19-TP620-I002-HES
61 | 94 | 65XA-8115 | 3049440 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G3 | 57-19-TP620-I003-HES
62 | 95 | 65XA-8116 | 3049426 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G3 | 57-19-TP620-I003-HES
63 | 96 | 65XA-8120 | 3046110 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G3 | 57-19-TP620-I003-HES
64 | 97 | 65XA-8121 | 3046111 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G3 | 57-19-TP620-I003-HES
65 | 98 | 65XA-8122 | 3050776 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G3 | 57-19-TP620-I003-HES
66 | 99 | 65XA-8123 | 3046109 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G4 | 57-19-TP620-I004-HES
67 | 100 | 65XA-8124 | 3046100 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G4 | 57-19-TP620-I004-HES
68 | 101 | 65XA-8125 | 3046123 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G4 | 57-19-TP620-I004-HES
69 | 102 | 65XA-8126 | 3046087 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G4 | 57-19-TP620-I004-HES
70 | 103 | 65XA-8127 | 3048807 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G4 | 57-19-TP620-I004-HES
71 | 104 | 65XA-8128 | 3046114 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G5 | 57-19-TP620-I005-HES
72 | 105 | 65XA-8129 | 3049413 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G5 | 57-19-TP620-I005-HES
73 | 106 | 65XA-8130 | 3033005 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G5 | 57-19-TP620-I005-HES
74 | 107 | 65XA-8131 | 3050769 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G5 | 57-19-TP620-I005-HES
75 | 108 | 65XA-8132 | 3046103 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G5 | 57-19-TP620-I005-HES
76 | 109 | 65XA-8133 | 3046105 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G6 | 57-19-TP620-I006-HES
77 | 110 | 65XA-8134 | 3048806 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G6 | 57-19-TP620-I006-HES
78 | 111 | 65XA-8135 | 3048817 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G6 | 57-19-TP620-I006-HES
79 | 114 | 65XA-8138 | 3048811 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G6 | 57-19-TP620-I006-HES
80 | 118 | 65XA-8142 | 3045776 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G6 | 57-19-TP620-I006-HES
81 | 119 | 65XA-8143 | 3048822 | CH4 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G6 | 57-19-TP620-I006-HES
82 | 92 | 65XA-8113 | 3048029 | H2 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G7 | 57-19-TP620-I007-HES
83 | 93 | 65XA-8114 | 3048052 | H2 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G7 | 57-19-TP620-I007-HES
84 | 84 | 65XA-8101 | AXGK2300196 | H2S 2W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G8 | 57-19-TP620-I008-HES
85 | 85 | 65XA-8102 | AXGK2300186 | H2S 2W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G8 | 57-19-TP620-I008-HES
86 | 86 | 65XA-8103 | AXGK2300187 | H2S 2W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G8 | 57-19-TP620-I008-HES
87 | 87 | 65XA-8104 | AXGK2300189 | H2S 2W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G8 | 57-19-TP620-I008-HES
88 | 88 | 65XA-8105 | AXGK2300192 | H2S 2W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G9 | 57-19-TP620-I009-HES
89 | 89 | 65XA-8106 | AXGK2300193 | H2S 2W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G9 | 57-19-TP620-I009-HES
90 | 115 | 65XA-8139 | AXGK2300195 | H2S 2W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G9 | 57-19-TP620-I009-HES
91 | 116 | 65XA-8140 | AXGK2300185 | H2S 2W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G9 | 57-19-TP620-I009-HES
92 | 117 | 65XA-8141 | AXGK2300191 | H2S 2W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G9 | 57-19-TP620-I009-HES
93 | 90 | 65XA-8111 | 3047363 | H2S 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G10 | 57-19-TP620-I010-HES
94 | 91 | 65XA-8112 | 3047367 | H2S 3W | 3_After TA | 57 | 19 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | G10 | 57-19-TP620-I010-HES
95 | 67 | 65H2-121 | 3048021 | H2 3W | 1_Before TA | 57 | 51 | 5A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y | Y | ABDE | H | 57-51-TP620-I001-HES
96 | 80 | 65H2S-129 | 3047358 | H2S 3W | 1_Before TA | 57 | 64 | 5A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | I1 | 57-64-TP620-I001-HES
97 | 79 | 65H2S-128 | 3046091 | H2S 3W | 1_Before TA | 57 | 64 | 5A | 620 |  | Y |  |  |  | Y | Y | Y | Y |  | DE | I2 | 57-64-TP620-I002-HES
98 | 23 | 65GA-201 | 3048819 | CH4 3W | 1_Before TA | 57 | 66 | 4A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | J1 | 57-66-TP620-I001-HES
99 | 49 | 65GA-270 | 3049432 | CH4 3W | 1_Before TA | 57 | 66 | 4A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | J1 | 57-66-TP620-I001-HES
100 | 50 | 65GA-274 | 3050790 | CH4 3W | 1_Before TA | 57 | 66 | 4A | 620 | Y | Y | Y |  |  | Y | Y | Y | Y |  | ABDE | J1 | 57-66-TP620-I001-HES
101 | 25 | 65GA-206 | 3048804 | CH4 3W | 1_Before TA | 57 | 71 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | K1 | 57-71-TP620-I001-HES
102 | 44 | 65GA-245 | 3046097 | CH4 3W | 1_Before TA | 57 | 71 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | K1 | 57-71-TP620-I001-HES
103 | 45 | 65GA-246 | 3049934 | CH4 3W | 1_Before TA | 57 | 71 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | K1 | 57-71-TP620-I001-HES
104 | 46 | 65GA-249 | 3046120 | CH4 3W | 1_Before TA | 57 | 71 | 4A | 620 | Y | Y | Y |  |  | Y | Y |  | Y |  | ABE | K2 | 57-71-TP620-I002-HES
105 | 24 | 65GA-205 | 3050796 | CH4 3W | 1_Before TA | 57 | 71 | 4A | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | K3 | 57-71-TP620-I003-HES
106 | 26 | 65GA-207 | 3048814 | CH4 3W | 1_Before TA | 57 | 71 | 4A | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | K3 | 57-71-TP620-I003-HES
107 | 33 | 65GA-225 | 3046117 | CH4 3W | 1_Before TA | 57 | 73 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | L1 | 57-73-TP620-I001-HES
108 | 36 | 65GA-229 | 3048827 | CH4 3W | 1_Before TA | 57 | 73 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | L1 | 57-73-TP620-I001-HES
109 | 37 | 65GA-230 | 3048832 | CH4 3W | 1_Before TA | 57 | 73 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | L1 | 57-73-TP620-I001-HES
110 | 38 | 65GA-231 | 3050792 | CH4 3W | 1_Before TA | 57 | 73 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | L1 | 57-73-TP620-I001-HES
111 | 39 | 65GA-232 | 3050774 | CH4 3W | 1_Before TA | 57 | 73 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | L2 | 57-73-TP620-I002-HES
112 | 40 | 65GA-233 | 3049435 | CH4 3W | 1_Before TA | 57 | 73 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | L2 | 57-73-TP620-I002-HES
113 | 41 | 65GA-234 | 3049428 | CH4 3W | 1_Before TA | 57 | 73 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | L2 | 57-73-TP620-I002-HES
114 | 42 | 65GA-236 | 3049427 | CH4 3W | 1_Before TA | 57 | 73 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | L2 | 57-73-TP620-I002-HES
115 | 34 | 65GA-226 | 3046118 | CH4 3W | 1_Before TA | 57 | 73 | 4A | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | L3 | 57-73-TP620-I003-HES
116 | 27 | 65GA-215 | 3050762 | CH4 3W | 1_Before TA | 57 | 75 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | M1 | 57-75-TP620-I001-HES
117 | 28 | 65GA-216 | 3046077 | CH4 3W | 1_Before TA | 57 | 75 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | M1 | 57-75-TP620-I001-HES
118 | 30 | 65GA-220 | 3049439 | CH4 3W | 1_Before TA | 57 | 75 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | M1 | 57-75-TP620-I001-HES
119 | 31 | 65GA-221 | 3050809 | CH4 3W | 1_Before TA | 57 | 75 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | M1 | 57-75-TP620-I001-HES
120 | 32 | 65GA-223 | 3046104 | CH4 3W | 1_Before TA | 57 | 75 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | M1 | 57-75-TP620-I001-HES
121 | 29 | 65GA-218 | 3046094 | CH4 3W | 1_Before TA | 57 | 75 | 4A | 620 | Y | Y | Y |  |  | Y | Y |  | Y |  | ABE | M2 | 57-75-TP620-I002-HES
122 | 47 | 65GA-250 | 3049416 | CH4 3W | 1_Before TA | 57 | 75 | 4A | 620 |  | Y |  |  |  | Y | Y | Y | Y |  | DE | M3 | 57-75-TP620-I003-HES
123 | 35 | 65GA-228 | 3049412 | CH4 3W | 1_Before TA | 57 | 75 | 4A | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | M4 | 57-75-TP620-I004-HES
124 | 43 | 65GA-240 | 3048826 | CH4 3W | 1_Before TA | 57 | 77 | 4A | 620 |  | Y |  |  |  | Y | Y |  |  |  |  | N1 | 57-77-TP620-I001-HES
125 | 48 | 65GA-267 | 3048803 | CH4 3W | 1_Before TA | 57 | 77 | 4A | 620 | Y | Y | Y |  |  | Y | Y |  | Y |  | ABE | N2 | 57-77-TP620-I002-HES
126 | 20 | 65GA-151B | 3050781 | CH4 3W | 2_TA | 57 | MCB | MCB | 620 |  | Y |  | Y |  | Y | Y |  | Y | Y | CE | O1 | 57-MCB-TP620-I001-HES
127 | 21 | 65GA-151C | 3050768 | CH4 3W | 2_TA | 57 | MCB | MCB | 620 |  | Y |  | Y |  | Y | Y |  | Y | Y | CE | O1 | 57-MCB-TP620-I001-HES
128 | 81 | 65XA-2631 | AXGK2300210 | H2S 2W | 2_TA | 57 | MCB | MCB | 620 |  | Y |  | Y |  | Y | Y |  | Y | Y | CE | O2 | 57-MCB-TP620-I002-HES
129 | 82 | 65XA-2632 | AXGK2300211 | H2S 2W | 2_TA | 57 | MCB | MCB | 620 |  | Y |  | Y |  | Y | Y |  | Y | Y | CE | O2 | 57-MCB-TP620-I002-HES
130 | 83 | 65XA-2633 | AXGK2300212 | H2S 2W | 2_TA | 57 | MCB | MCB | 620 |  | Y |  | Y |  | Y | Y |  | Y | Y | CE | O2 | 57-MCB-TP620-I002-HES
131 | 134 | 65XA-8193A | 3049441 | CH4 3W | 2_TA | 57 | MG3 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | P2 | 57-MG3-TP620-I002-HES
132 | 135 | 65XA-8193B | 3049420 | CH4 3W | 2_TA | 57 | MG3 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | P2 | 57-MG3-TP620-I002-HES
133 | 136 | 65XA-8193C | 3048818 | CH4 3W | 2_TA | 57 | MG3 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | P2 | 57-MG3-TP620-I002-HES
134 | 131 | 65XA-8190A | AXGK2300203 | H2S 2W | 2_TA | 57 | MG3 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | P1 | 57-MG3-TP620-I001-HES
135 | 132 | 65XA-8190B | AXGK2300204 | H2S 2W | 2_TA | 57 | MG3 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | P1 | 57-MG3-TP620-I001-HES
136 | 133 | 65XA-8190C | AXGK2300205 | H2S 2W | 2_TA | 57 | MG3 | 6 | 620 |  | Y |  |  |  | Y | Y |  | Y |  | E | P1 | 57-MG3-TP620-I001-HES
137 | 137 | MCB-FGS-001 SYSTEM, MCB-FGS-001 MDF |  | Cab | 2_TA | 57 | MCB | 1A,1B | 620 |  |  |  |  | Y | [7 empty] | 57-MCB-TP620-I003-HES
138 | 138 | OMS-FGS-001 SYSTEM, OMS-FGS-001 MDF |  | Cab | 2_TA | 57 | OMS | 4A | 620 |  |  |  |  | Y | [7 empty] | 57-OMS-TP620-I001-HES
139 | 139 | SS1-FGS-001 SYSTEM, SS1-FGS-001 MDF |  | Cab | 2_TA | 57 | SS01 | 4 | 620 |  |  |  |  | Y | [7 empty] | 57-SS1-TP620-I001-HES
140 | 140 | SS7-FGS-001 SYSTEM, SS7-FGS-001 MDF |  | Cab | 2_TA | 57 | SS07 | 4 | 620 |  |  |  |  | Y | [7 empty] | 57-SS7-TP620-I001-HES
141 | 141 | 8-FGS-001 SYSTEM, 8-FGS-002 SYSTEM, 8-MDF-001, 8-MDF-002, 8-MDF-003 |  | Cab | 2_TA | 57 | MG3 | 6 | 620 |  |  |  |  | Y | [7 empty] | 57-MG3-TP620-I003-HES

## Master (GD)_Detailed ITR_BU
Internal
[11 empty] | 111A |  |  |  |  | 101A |  |  |  | 104A | [6 empty] | 111B
Sorted No. | Tag No. | S/N | GD TYPE | WINDOW | UNIT | AREA | SUBSYSTEM | SUB-SUBSYSTEM | CATEGORY | TEST PACK NO | MANUFACTURER | SIZE (KG) | MODEL NO | Set point pressure | Datasheet | Cable Size | Voltage | Cable from (Int JB) | Cable To (GD) | IP Rating (JB) | Manufacturer | DWG no. | EX Class | Location | Serial No. | Type | Mode of Detection | EX Protection | Model No | Serial No. | Signal Range (mA, EU) | IP Rating | Manufacturer | DWG No.
1 | 65GA-106, 65GA-107, 65GA-110, 65GA-115 | 3048820 (106), 3046101 (107), 3046098 (110), 3050804 (115) | CH4 3W | OSTA 23 | 11 | 1A | 620 | 622 | 4 | 57-11-TP620-I001-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | 1Tr x 1.5mm2, 3 Cores | 500V | 11-JB-GA106, 11-JB-GA107, 11-JB-GA110, 11-JB-GA115 | 65GA-106, 65GA-107, 65GA-110, 65GA-115 | IP66 | PHOENIX CONTACT | RESET-EXE-HES-00-MCI-MAF-4003 | Ex II 2G Ex e II T6/T5 | Area 1A / Unit 11 |  | Wall mount | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3048820 (106), 3046101 (107), 3046098 (110), 3050804 (115) | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-1A-INC-LST-4001
2 | 65GA-108, 65GA-121 | 3046099 (108), 3050767 (121) | CH4 3W | OSTA 23 | 11 | 1A | 620 | 622 | 2 | 57-11-TP620-I002-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3046099 (108), 3050767 (121) | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-1A-INC-LST-4001
3 | 65GA-111, 65GA-116, 65GA-119, 65GA-120 | 3050785 (111), 3048810 (116), 3048828 (119), 3049423 (120) | CH4 3W | OSTA 23 | 11 | 1A | 620 | 622 | 2 | 57-11-TP620-I003-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3050785 (111), 3048810 (116), 3048828 (119), 3049423 (120) | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-1A-INC-LST-4001
4 | 65H2-120 | 3048032 | H2 3W | OSTA 23 | 11 | 1A | 620 | 622 | 2 | 57-11-TP620-I004-HES | GASENSOR | 4.8KG | HE-CT8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, low temperature catalytic bead | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CT8900 | 3048032 | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-1A-INC-LST-4001
5 | 65GA-601 | AXGK2300184 | H2S 2W | OSTA 23 | 11 | 1A | 620 | 622 | 2 | 57-11-TP620-I005-HES | GASTRON | 2KG | GTD-2000TX | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | GTD-2000TX | AXGK2300184 | 0-20mA, 0-50 PPM | IP66 | GASTRON | RESET-EXE-HES-1A-INC-LST-4001
6 | 65H2S-101, 65H2S-102, 65H2S-103, 65H2S-104, 65H2S-107 | 3041318 (101), 3041383 (102), 3046075 (103), 3046084 (104), 3047355 (107) | H2S 3W | OSTA 23 | 11 | 1A | 620 | 622 | 4 | 57-11-TP620-I006-HES | GASENSOR | 4.8KG | HE-CE-8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | 1Tr x 1.5mm2, 3 Cores | 500V | 11-JB-H2S101, 11-JB-H2S102, 11-JB-H2S103, 11-JB-H2S104, 11-JB-H2S107 | 65H2S-101, 65H2S-102, 65H2S-103, 65H2S-104, 65H2S-107 | IP66 | PHOENIX CONTACT | RESET-EXE-HES-00-MCI-MAF-4003 | Ex II 2G Ex e II T6/T5 | Area 1A / Unit 11 |  | Wall mount | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CE-8900 | 3041318 (101), 3041383 (102), 3046075 (103), 3046084 (104), 3047355 (107) | 0-22mA, 0-50 PPM | IP66 | GASENSOR | RESET-EXE-HES-1A-INC-LST-4001
7 | 65GA-129 | 3048816 | CH4 3W | OSTA 23 | 12 | 1B | 620 | 622 | 2 | 57-12-TP620-I001-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3048816 | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-1B-INC-LST-4001
8 | 65H2-104, 65H2-112, 65H2-113, 65H2-114, 65H2-115 | 3048022 (104), 3048033 (112), 3048017 (113), 3048030 (114), 3048020 (115) | H2 3W | OSTA 23 | 12 | 1B | 620 | 622 | 2 | 57-12-TP620-I002-HES | GASENSOR | 4.8KG | HE-CT8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, low temperature catalytic bead | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CT8900 | 3048022 (104), 3048033 (112), 3048017 (113), 3048030 (114), 3048020 (115) | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-1B-INC-LST-4001
9 | 65H2-101, 65H2-103 | 3048028 (101), 3048010 (103) | H2 3W | OSTA 23 | 12 | 1B | 620 | 622 | 2 | 57-12-TP620-I003-HES | GASENSOR | 4.8KG | HE-CT8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, low temperature catalytic bead | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CT8900 | 3048028 (101), 3048010 (103) | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-1B-INC-LST-4001
10 | 65H2S-118, 65H2S-119, 65H2S-120 | 3047395 (118), 3046078 (119), 3046088 (120) | H2S 3W | OSTA 23 | 12 | 1B | 620 | 622 | 4 | 57-12-TP620-I004-HES | GASENSOR | 4.8KG | HE-CE-8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | 1Tr x 1.5mm2, 3 Cores | 500V | 12-JB-H2S118, 12-JB-H2S119, 12-JB-H2S120 | 65H2S-118, 65H2S-119, 65H2S-120 | IP66 | PHOENIX CONTACT | RESET-EXE-HES-00-MCI-MAF-4003 | Ex II 2G Ex e II T6/T5 | Area 1B / Unit 12 |  | Wall mount | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CE-8900 | 3047395 (118), 3046078 (119), 3046088 (120) | 0-22mA, 0-50 PPM | IP66 | GASENSOR | RESET-EXE-HES-1B-INC-LST-4001
11 | 65H2S-111 | 3047309 | H2S 3W | OSTA 23 | 12 | 1B | 620 | 622 | 2 | 57-12-TP620-I005-HES | GASENSOR | 4.8KG | HE-CE-8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CE-8900 | 3047309 | 0-22mA, 0-50 PPM | IP66 | GASENSOR | RESET-EXE-HES-1B-INC-LST-4001
12 | 65H2S-114 | 3046083 | H2S 3W | OSTA 23 | 12 | 1B | 620 | 622 | 2 | 57-12-TP620-I006-HES | GASENSOR | 4.8KG | HE-CE-8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CE-8900 | 3046083 | 0-22mA, 0-50 PPM | IP66 | GASENSOR | RESET-EXE-HES-1B-INC-LST-4001
13 | 65GA-170 | 3050789 | CH4 3W | OSTA 23 | 13 | 1B | 620 | 622 | 2 | 57-13-TP620-I001-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3050789 | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-1B-INC-LST-4001
14 | 65GA-132, 65GA-137 | 3048813 (132), 3048808 (137) | CH4 3W | OSTA 23 | 13 | 1B | 620 | 622 | 4 | 57-13-TP620-I002-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | 1Tr x 1.5mm2, 3 Cores | 500V | 13-JB-GA132, 13-JB-GA137 | 65GA-132, 65GA-137 | IP66 | PHOENIX CONTACT | RESET-EXE-HES-00-MCI-MAF-4003 | Ex II 2G Ex e II T6/T5 | Area 1B / Unit 13 |  | Wall mount | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3048813 (132), 3048808 (137) | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-1B-INC-LST-4001
15 | 65GA-134, 65GA-139 | 3046115 (134), 3048830 (139) | CH4 3W | OSTA 23 | 13 | 1B | 620 | 622 | 2 | 57-13-TP620-I003-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3046115 (134), 3048830 (139) | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-1B-INC-LST-4001
16 | 65H2-118 | 3048025 | H2 3W | OSTA 23 | 13 | 1B | 620 | 622 | 2 | 57-13-TP620-I004-HES | GASENSOR | 4.8KG | HE-CT8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, low temperature catalytic bead | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CT8900 | 3048025 | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-1B-INC-LST-4001
17 | 65H2-106, 65H2-116 | 3048024 (106), 3048018 (116) | H2 3W | OSTA 23 | 13 | 1B | 620 | 622 | 4 | 57-13-TP620-I005-HES | GASENSOR | 4.8KG | HE-CT8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | 1Tr x 1.5mm2, 3 Cores | 500V | 13-JB-H2106, 13-JB-H2116 | 65H2-106, 65H2-116 | IP66 | PHOENIX CONTACT | RESET-EXE-HES-00-MCI-MAF-4003 | Ex II 2G Ex e II T6/T5 | Area 1B / Unit 13 |  | Wall mount | Continuous diffusion, low temperature catalytic bead | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CT8900 | 3048024 (106), 3048018 (116) | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-1B-INC-LST-4001
18 | 65H2-107, 65H2-108, 65H2-109, 65H2-111 | 3048053 (107), 3048027 (108), 3048006 (109), 3048026 (111) | H2 3W | OSTA 23 | 13 | 1B | 620 | 622 | 2 | 57-13-TP620-I006-HES | GASENSOR | 4.8KG | HE-CT8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, low temperature catalytic bead | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CT8900 | 3048053 (107), 3048027 (108), 3048006 (109), 3048026 (111) | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-1B-INC-LST-4001
19 | 65GA-125, 65GA-126, 65GA-127, 65GA-128 | 3046113 (125), 3048829 (126), 3049419 (127), 3049437 (128) | CH4 3W | OSTA 23 | 14 | 1A | 620 | 622 | 4 | 57-14-TP620-I001-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | 1Tr x 1.5mm2, 3 Cores | 500V | 14-JB-GA125, 14-JB-GA126, 14-JB-GA127, 14-JB-GA128 | 65GA-125, 65GA-126, 65GA-127, 65GA-128 | IP66 | PHOENIX CONTACT | RESET-EXE-HES-00-MCI-MAF-4003 | Ex II 2G Ex e II T6/T5 | Area 1A / Unit 14 |  | Wall mount | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3046113 (125), 3048829 (126), 3049419 (127), 3049437 (128) | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-1A-INC-LST-4001
20 | 65H2S-122 | 3047392 | H2S 3W | OSTA 23 | 15 | 1A | 620 | 622 | 2 | 57-15-TP620-I001-HES | GASENSOR | 4.8KG | HE-CE-8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CE-8900 | 3047392 | 0-22mA, 0-50 PPM | IP66 | GASENSOR | RESET-EXE-HES-1A-INC-LST-4001
21 | 65XA-8154 | 3046116 | CH4 3W | OSTA 24 | 18 | 6 | 620 | 622 | 2 | 57-18-TP620-I001-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3046116 | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-06-INC-LST-4003
22 | 65XA-8157, 65XA-8160, 65XA-8162 | 3048812 (8157), 3050783 (8160), 3049417 (8162) | CH4 3W | OSTA 24 | 18 | 6 | 620 | 622 | 2 | 57-18-TP620-I002-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3048812 (8157), 3050783 (8160), 3049417 (8162) | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-06-INC-LST-4003
23 | 65XA-8155 | 3048009 | H2 3W | OSTA 24 | 18 | 6 | 620 | 622 | 2 | 57-18-TP620-I003-HES | GASENSOR | 4.8KG | HE-CT8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, low temperature catalytic bead | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CT8900 | 3048009 | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-06-INC-LST-4003
24 | 65XA-8159 | 3047997 | H2 3W | OSTA 24 | 18 | 6 | 620 | 622 | 2 | 57-18-TP620-I004-HES | GASENSOR | 4.8KG | HE-CT8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, low temperature catalytic bead | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CT8900 | 3047997 | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-06-INC-LST-4003
25 | 65XA-8151, 65XA-8156 | AXGK2300194 (8151), AXGK2300190 (8156) | H2S 2W | OSTA 24 | 18 | 6 | 620 | 622 | 2 | 57-18-TP620-I005-HES | GASTRON | 2KG | GTD-2000TX | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | GTD-2000TX | AXGK2300194 (8151), AXGK2300190 (8156) | 0-20mA, 0-50 PPM | IP66 | GASTRON | RESET-EXE-HES-06-INC-LST-4003
26 | 65XA-8152, 65XA-8153 | AXGK2300197 (8152), AXGK2300188 (8153) | H2S 2W | OSTA 24 | 18 | 6 | 620 | 622 | 2 | 57-18-TP620-I006-HES | GASTRON | 2KG | GTD-2000TX | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | GTD-2000TX | AXGK2300197 (8152), AXGK2300188 (8153) | 0-20mA, 0-50 PPM | IP66 | GASTRON | RESET-EXE-HES-06-INC-LST-4003
27 | 65XA-8144 | 3050764 | CH4 3W | TA 2024 | 19 | 6 | 620 | 622 | 2 | 57-19-TP620-I001-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3050764 | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-06-INC-LST-4003
28 | 65XA-8136, 65XA-8137 | 3050787 (8136), 3046095 (8137) | CH4 3W | OSTA 24 | 19 | 6 | 620 | 622 | 2 | 57-19-TP620-I002-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3050787 (8136), 3046095 (8137) | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-06-INC-LST-4003
29 | 65XA-8115, 65XA-8116, 65XA-8120, 65XA-8121, 65XA-8122 | 3049440 (8115), 3049426 (8116), 3046110 (8120), 3046111 (8121), 3050776 (8122) | CH4 3W | OSTA 24 | 19 | 6 | 620 | 622 | 2 | 57-19-TP620-I003-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3049440 (8115), 3049426 (8116), 3046110 (8120), 3046111 (8121), 3050776 (8122) | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-06-INC-LST-4003
30 | 65XA-8123, 65XA-8124, 65XA-8125, 65XA-8126, 65XA-8127 | 3046109 (8123), 3046100 (8124), 3046123 (8125), 3046087 (8126), 3048807 (8127) | CH4 3W | OSTA 24 | 19 | 6 | 620 | 622 | 2 | 57-19-TP620-I004-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3046109 (8123), 3046100 (8124), 3046123 (8125), 3046087 (8126), 3048807 (8127) | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-06-INC-LST-4003
31 | 65XA-8128, 65XA-8129, 65XA-8130, 65XA-8131, 65XA-8132 | 3046114 (8128), 3049413 (8129), 3033005 (8130), 3050769 (8131), 3046103 (8132) | CH4 3W | OSTA 24 | 19 | 6 | 620 | 622 | 2 | 57-19-TP620-I005-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3046114 (8128), 3049413 (8129), 3033005 (8130), 3050769 (8131), 3046103 (8132) | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-06-INC-LST-4003
32 | 65XA-8133, 65XA-8134, 65XA-8135, 65XA-8138, 65XA-8142, 65XA-8143 | 3046105 (8133),3048806 (8134), 3048817 (8135), 3048811 (8138), 3045776 (8142), 3048822 (8143) | CH4 3W | OSTA 24 | 19 | 6 | 620 | 622 | 2 | 57-19-TP620-I006-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3046105 (8133),3048806 (8134), 3048817 (8135), 3048811 (8138), 3045776 (8142), 3048822 (8143) | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-06-INC-LST-4003
33 | 65XA-8113, 65XA-8114 | 3048029 (8113), 3048052 (8114) | H2 3W | OSTA 24 | 19 | 6 | 620 | 622 | 2 | 57-19-TP620-I007-HES | GASENSOR | 4.8KG | HE-CT8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, low temperature catalytic bead | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CT8900 | 3048029 (8113), 3048052 (8114) | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-06-INC-LST-4003
34 | 65XA-8101, 65XA-8102, 65XA-8103, 65XA-8104 | AXGK2300196 (8101), AXGK2300186 (8102), AXGK2300187 (8103), AXGK2300189 (8104) | H2S 2W | OSTA 24 | 19 | 6 | 620 | 622 | 2 | 57-19-TP620-I008-HES | GASTRON | 2KG | GTD-2000TX | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | GTD-2000TX | AXGK2300196 (8101), AXGK2300186 (8102), AXGK2300187 (8103), AXGK2300189 (8104) | 0-20mA, 0-50 PPM | IP66 | GASTRON | RESET-EXE-HES-06-INC-LST-4003
35 | 65XA-8105, 65XA-8106, 65XA-8139, 65XA-8140, 65XA-8141 | AXGK2300192 (8105), AXGK2300193 (8106), AXGK2300195 (8139), AXGK2300185 (8140), AXGK2300191 (8141) | H2S 2W | OSTA 24 | 19 | 6 | 620 | 622 | 2 | 57-19-TP620-I009-HES | GASTRON | 2KG | GTD-2000TX | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | GTD-2000TX | AXGK2300192 (8105), AXGK2300193 (8106), AXGK2300195 (8139), AXGK2300185 (8140), AXGK2300191 (8141) | 0-20mA, 0-50 PPM | IP66 | GASTRON | RESET-EXE-HES-06-INC-LST-4003
36 | 65XA-8111, 65XA-8112 | 3047363 (8111), 3047367 (8112) | H2S 3W | OSTA 24 | 19 | 6 | 620 | 622 | 2 | 57-19-TP620-I010-HES | GASENSOR | 4.8KG | HE-CE-8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CE-8900 | 3047363 (8111), 3047367 (8112) | 0-22mA, 0-50 PPM | IP66 | GASENSOR | RESET-EXE-HES-06-INC-LST-4003
37 | 65H2-121 | 3048021 | H2 3W | OSTA 23 | 51 | 5A | 620 | 622 | 4 | 57-51-TP620-I001-HES | GASENSOR | 4.8KG | HE-CT8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | 1Tr x 1.5mm2, 3 Cores | 500V | 51-JB-H2121 | 65H2-121 | IP66 | PHOENIX CONTACT | RESET-EXE-HES-00-MCI-MAF-4003 | Ex II 2G Ex e II T6/T5 | Area 5A / Unit 51 |  | Wall mount | Continuous diffusion, low temperature catalytic bead | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CT8900 | 3048021 | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-5A-INC-LST-4001
38 | 65H2S-129 | 3047358 | H2S 3W | OSTA 23 | 64 | 5A | 620 | 622 | 4 | 57-64-TP620-I001-HES | GASENSOR | 4.8KG | HE-CE-8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | 1Tr x 1.5mm2, 3 Cores | 500V | 64-JB-H2S129 | 65H2S-129 | IP66 | PHOENIX CONTACT | RESET-EXE-HES-00-MCI-MAF-4003 | Ex II 2G Ex e II T6/T5 | Area 5A / Unit 64 |  | Wall mount | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CE-8900 | 3047358 | 0-22mA, 0-50 PPM | IP66 | GASENSOR | RESET-EXE-HES-5A-INC-LST-4001
39 | 65H2S-128 | 3046091 | H2S 3W | OSTA 23 | 64 | 5A | 620 | 622 | 2 | 57-64-TP620-I002-HES | GASENSOR | 4.8KG | HE-CE-8900 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | HE-CE-8900 | 3046091 | 0-22mA, 0-50 PPM | IP66 | GASENSOR | RESET-EXE-HES-5A-INC-LST-4001
40 | 65GA-201, 65GA-270, 65GA-274 | 3048819 (201), 3049432 (270), 3050790 (274) | CH4 3W | OSTA 23 | 66 | 4A | 620 | 622 | 4 | 57-66-TP620-I001-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | 1Tr x 1.5mm2, 3 Cores | 500V | 66-JB-GA201, 66-JB-GA270, 66-JB-GA274 | 65GA-201, 65GA-270, 65GA-274 | IP66 | PHOENIX CONTACT | RESET-EXE-HES-00-MCI-MAF-4003 | Ex II 2G Ex e II T6/T5 | Area 4A / Unit 66 |  | Wall mount | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3048819 (201), 3049432 (270), 3050790 (274) | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-4A-INC-LST-4001
41 | 65GA-206, 65GA-245, 65GA-246 | 3048804 (206), 3046097 (245), 3049934 (246) | CH4 3W | OSTA 23 | 71 | 4A | 620 | 622 | 2 | 57-71-TP620-I001-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3048804 (206), 3046097 (245), 3049934 (246) | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-4A-INC-LST-4001
42 | 65GA-249 | 3046120 | CH4 3W | OSTA 23 | 71 | 4A | 620 | 622 | 4 | 57-71-TP620-I002-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | 1Tr x 1.5mm2, 3 Cores | 500V | 66-JB-GA249 | 65GA-249 | IP66 | PHOENIX CONTACT | RESET-EXE-HES-00-MCI-MAF-4003 | Ex II 2G Ex e II T6/T5 | Area 4A / Unit 71 |  | Wall mount | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3046120 | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-4A-INC-LST-4001
43 | 65GA-205, 65GA-207 | 3050796 (205), 3048814 (207) | CH4 3W | OSTA 23 | 71 | 4A | 620 | 622 | 2 | 57-71-TP620-I003-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3050796 (205), 3048814 (207) | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-4A-INC-LST-4001
44 | 65GA-225, 65GA-229, 65GA-230, 65GA-231 | 3046117 (225), 3048827 (229), 3048832 (230), 3050792 (231) | CH4 3W | OSTA 23 | 73 | 4A | 620 | 622 | 2 | 57-73-TP620-I001-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3046117 (225), 3048827 (229), 3048832 (230), 3050792 (231) | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-4A-INC-LST-4001
45 | 65GA-232, 65GA-233, 65GA-234, 65GA-236 | 3050774 (232), 3049435 (233), 3049428 (234), 3049427 (236) | CH4 3W | OSTA 23 | 73 | 4A | 620 | 622 | 2 | 57-73-TP620-I002-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3050774 (232), 3049435 (233), 3049428 (234), 3049427 (236) | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-4A-INC-LST-4001
46 | 65GA-226 | 3046118 | CH4 3W | OSTA 23 | 73 | 4A | 620 | 622 | 2 | 57-73-TP620-I003-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3046118 | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-4A-INC-LST-4001
47 | 65GA-215, 65GA-216, 65GA-220, 65GA-221, 65GA-223 | 3050762 (215), 3046077 (216), 3049439 (220), 3050809 (221), 3046104 (223) | CH4 3W | OSTA 23 | 75 | 4A | 620 | 622 | 2 | 57-75-TP620-I001-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3050762 (215), 3046077 (216), 3049439 (220), 3050809 (221), 3046104 (223) | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-4A-INC-LST-4001
48 | 65GA-218 | 3046094 | CH4 3W | OSTA 23 | 75 | 4A | 620 | 622 | 4 | 57-75-TP620-I002-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | 1Tr x 1.5mm2, 3 Cores | 500V | 66-JB-GA218 | 65GA-218 | IP66 | PHOENIX CONTACT | RESET-EXE-HES-00-MCI-MAF-4003 | Ex II 2G Ex e II T6/T5 | Area 4A / Unit 75 |  | Wall mount | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3046094 | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-4A-INC-LST-4001
49 | 65GA-250 | 3049416 | CH4 3W | OSTA 23 | 75 | 4A | 620 | 622 | 2 | 57-75-TP620-I003-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3049416 | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-4A-INC-LST-4001
50 | 65GA-228 | 3049412 | CH4 3W | OSTA 23 | 75 | 4A | 620 | 622 | 2 | 57-75-TP620-I004-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3049412 | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-4A-INC-LST-4001
51 | 65GA-240 | 3048826 | CH4 3W | OSTA 23 | 77 | 4A | 620 | 622 | 2 | 57-77-TP620-I001-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3048826 | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-4A-INC-LST-4001
52 | 65GA-267 | 3048803 | CH4 3W | OSTA 23 | 77 | 4A | 620 | 622 | 4 | 57-77-TP620-I002-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | 1Tr x 1.5mm2, 3 Cores | 500V | 66-JB-GA267 | 65GA-267 | IP66 | PHOENIX CONTACT | RESET-EXE-HES-00-MCI-MAF-4003 | Ex II 2G Ex e II T6/T5 | Area 4A / Unit 77 |  | Wall mount | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3048803 | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-4A-INC-LST-4001
53 | 65GA-151B, 65GA-151C | 3050781 (151B), 3050768 (151C) | CH4 3W | TA 2024 | MCB | MCB | 620 | 622 | 2 | 57-MCB-TP620-I001-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3050781 (151B), 3050768 (151C) | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-93-INC-LST-4003
54 | 65XA-2631, 65XA-2632, 65XA-2633 | AXGK2300210 (2631), AXGK2300211 (2632), AXGK2300212 (2633) | H2S 2W | TA 2024 | MCB | MCB | 620 | 622 | 2 | 57-MCB-TP620-I002-HES | GASTRON | 2KG | GTD-2000TX | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | GTD-2000TX | AXGK2300210 (2631), AXGK2300211 (2632), AXGK2300212 (2633) | 0-20mA, 0-50 PPM | IP66 | GASTRON | RESET-EXE-HES-93-INC-LST-4003
55 | 65XA-8190A, 65XA-8190B, 65XA-8190C | AXGK2300203 (8190A), AXGK2300204 (8190B), AXGK2300205 (8190C) | H2S 2W | TA 2024 | SCR8 | 6 | 620 | 622 | 2 | 57-SCR8-TP620-I001-HES | GASTRON | 2KG | GTD-2000TX | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Electrochemical cell | ATEX / IECEx Ex db ib IIC T6 Gb | GTD-2000TX | AXGK2300203 (8190A), AXGK2300204 (8190B), AXGK2300205 (8190C) | 0-20mA, 0-50 PPM | IP66 | GASTRON | RESET-EXE-HES-06-INC-LST-4003
56 | 65XA-8193A, 65XA-8193B, 65XA-8193C | 3049441 (8193A), 3049420 (8193B), 3048818 (8193C) | CH4 3W | TA 2024 | SCR8 | 6 | 620 | 622 | 2 | 57-SCR8-TP620-I002-HES | GASENSOR | 6.8KG | HE-IR800 | N/A | RESET-EXE-HES-00-ENG-TDS-4002 | [11 empty] | Continuous diffusion, Nondispersive infrared (NDIR ) | ATEX / IECEx Ex db ib IIC T6 Gb | HE-IR800 | 3049441 (8193A), 3049420 (8193B), 3048818 (8193C) | 0-22mA, 0-100% LEL | IP66 | GASENSOR | RESET-EXE-HES-06-INC-LST-4003
57 | MCB-FGS-001 SYSTEM, MCB-FGS-001 MDF |  |  | TA 2024 | MCB | MCB | 620 | 622 | P | 57-MCB-TP620-I003-HES
58 | OMS-FGS-001 SYSTEM, OMS-FGS-001 MDF |  |  | TA 2024 | OMS | 4A | 620 | 622 | P | 57-OMS-TP620-I001-HES
59 | SS1-FGS-001 SYSTEM, SS1-FGS-001 MDF |  |  | TA 2024 | SS01 | 4A | 620 | 622 | P | 57-SS1-TP620-I001-HES
60 | SS7-FGS-001 SYSTEM, SS7-FGS-001 MDF |  |  | TA 2024 | SS07 | 4A | 620 | 622 | P | 57-SS7-TP620-I001-HES
61 | 8-FGS-001 SYSTEM, 8-FGS-002 SYSTEM, 8-MDF-001, 8-MDF-002, 8-MDF-003 |  |  | TA 2024 | SCR8 | 6 | 620 | 622 | P | 57-SCR8-TP620-I003-HES